## Slide 1
Chapter 7:
Modeling Network Components

## Slide 2
Overview of this chapter
Previous chapter: load and generation are at the same location
However, in most power systems, they are connected by vast networks
This chapter: develop models of the network components
  Lines
  Transformers
  Substations (locations where components connect)
Next chapter: combine these models into an overall network model

## Slide 3
Model of a unit of length of AC line
Resistance per unit of length:
: resistivity of the conducting material (
effective area of a cross-section of the conductor ()
Effective area because current is not uniformly distributed in an AC conductor due to skin effect

## Slide 4
Why is knowing the resistance of a line important?
Resistance affects losses
Losses determine temperature rise in the conductor
Overhead line: temperature determines the sag of the conductor
  If a conductor sags too much, it will get too close to a grounded object (e.g., a tree) and cause a fault
Underground cable: excessive temperature damages the insulation and will over time cause a fault

## Slide 5
Aluminum Conductor Steel Reinforced (ACSR)
Common type of conductor used for overhead transmission and distribution lines
Outer aluminum strands support conduction
Inner steel strands provide tensile strength and reduce sagging
Many different sizes and configuration of strands, each with its own bird name.

## Slide 6
Magnetic field
Current in line creates a magnetic field
Model magnetic field with series inductance per unit of length
Electromagnetic theory  formulas for calculating as a function of the geometry of the line
  Size of the conductors
  Spacing of the conductors
These formulas are encapsulated in tables and computer tools
Inductive series reactance per unit of length
For transmission lines:

## Slide 7
Electric field
Voltage applied to a line creates an electric field
Model electric field with a shunt capacitance per unit of length
Electromagnetic theory  formulas for calculating as a function of the geometry of the line
  Size of the conductors
  Spacing of the conductors
Capacitive shunt admittance per unit of length:
Shunt admittance of underground cable >> shunt admittance of overhead line

## Slide 8
Corona effect
Strong electric field at the surface of the conductor  ionization of the air
Causes
  Radio interference
  Power losses
  Buzzing noise
Modeled as shunt conductance per unit of length
Only significant for EHV lines (765 kV)

## Slide 9
Model of a unit length of line

## Slide 10
Rigorous model of a line
Useful for studying wave propagation along the line

## Slide 11
model of a medium length line (< 300 km)
: length of the line

## Slide 12
model of a line neglecting corona losses
: length of the line

## Slide 13
Model of a short overhead line (< 25 km)
: length of the line

## Slide 14
Model that we will use when we want to keep things simple…

## Slide 15
Example 7.1
A three-phase 345-kV line is 250 km long. Its line parameters are:
; ; ; is negligible
Using a 100 MVA base, calculate the per unit parameters of its -equivalent circuit.
Hence:

## Slide 16
Example 7.2
A generator operating at nominal voltage is connected to the sending end of the transmission line of example 7.1. The receiving end is left open-ended. Calculate the voltage at the receiving end as well as the active and reactive powers supplied by this generator.
-

## Slide 17
Example 7.2
-
The complex power supplied by the generator is then:
 Generator produces 626 kW of active power and absorbs 61.27 MVar

## Slide 18
Example 7.3
A load of 125 MW at 0.85 p.f. lagging is connected at the receiving end of the line of Example 7.1. If the receiving end voltage , what is the voltage at the sending end? How much active and reactive power does the generator produce?
-
Load

## Slide 19
Example 7.3
-
Load
The generator thus supplies 125 MW to the load and 11 MW of line losses, as well as 39.6 Mvar.

## Slide 20
DC Lines
The power electronics converter allow for precise control of the active and reactive power
For our purposes, modeled as active and reactive power extractions at one end and injections at the other end
Converter 1
+
-
Reg
Converter 2
Grid 2
Grid 1
dc link

## Slide 21
Single-phase transformers
Magnetic core
Primary
Assume same flux
links both windings
Magnetic flux
Secondary

## Slide 22
Voltages in an ideal transformer
In terms of phasors:
 The primary and secondary voltages are in phase

## Slide 23
Ideal transformer in the phasor domain

## Slide 24
Currents in an ideal transformer
Ideal transformer  no active or reactive power losses
Power input = power output

## Slide 25
Impedances in an ideal transformer
 Secondary impedance referred to the primary

## Slide 26
Example 7.4
The nameplate of a single-phase transformer indicates that its primary voltage rating is 240V and its secondary voltage rating is 12V. If the primary winding is connected to a 200V source and the secondary winding to a 5+j2 impedance, calculate the secondary voltage, the currents in the primary and secondary windings and the active and reactive powers delivered by this transformer. Assume that the transformer is ideal.
Alternatively:

## Slide 27: Actual Transformer
Actual transformer
  Losses in windings (copper losses)
  Losses in the core (iron losses)
  Magnetizing current
  Leakage flux
Ideal transformer
  No losses
  Infinite permeability
  Same flux across both windings

## Slide 28: Modeling an Actual Transformer
Start from ideal transformer model
Add components to represent:
  Leakage flux
  Losses in windings (copper losses)
  Magnetizing current
  Losses in the core (iron losses)

## Slide 29: Leakage flux
Ideal Transformer
Some flux crosses the primary winding but not the secondary winding and vice-versa
Modeled by adding inductances on the primary and secondary windings to represent these leakage fluxes

## Slide 30: Windings Resistance
Windings always have some resistance
“Copper losses”

## Slide 31: Magnetizing Current
Magnetic flux:
ross section of magnetic core
B: Magnetic flux density
Permeability of core material
H: Magnetic field
H Ni: magneto-motive force (mmf)
air
iron
ideal

## Slide 32: Magnetizing Current
If the core were made of ideal magnetic material, we would not need any current to create the flux
Even when the core is made of a good magnetic material, such as iron, we need some current to create this flux
In an actual transformer, not all the primary current is transformed in a secondary current according to
iron
ideal

## Slide 33: Modeling the magnetizing current
iron
ideal
Magnetizing current
Magnetizing reactance

## Slide 34: Magnetization Curve
Saturation
Magnetic
material
: magnetic field
: magnetic flux
: flux density

## Slide 35: Remanent magnetism
Start with material with no magnetic field
Create a dc magnetic field --> the flux increases
Remove the magnetic field
When the magnetic field is zero, the flux is not zero
We have a permanent magnet
Remanent magnetism

## Slide 36: Hysteresis losses
Magnetic
material
Remanent
magnetism
If we apply an ac voltage to such materials, the flux follows a hysteresis loop at every cycle
An amount of energy proportional to the area of the hysteresis loop is dissipated at every cycle

## Slide 37: Eddy current losses
Lenz’s law:
  Variable magnetic flux induces currents that tend to oppose the change in flux
Such currents are induced in the iron of the magnetic core
Source: www.eenewsanalog.com/news/difference-between-inductive-proximity-displacement-and-eddy-current-sensors-0

## Slide 38: Eddy current losses
These circulating currents (eddy currents) create losses in the core
Building the magnetic core using laminations reduces the eddy current losses by reducing the magnitude of the eddy currents

## Slide 39: Modeling the core losses
“Core losses” or “iron losses” = hysteresis losses + eddy current losses)

## Slide 40
Actual transformer model
Ideal transformer
: magnetizing current
: magnetic core losses
: primary winding leakage flux
: secondary winding leakage flux
: primary winding resistance
: secondary winding resistance

## Slide 41
Actual transformer model
Voltage ratios:
Current ratios:
but
but
Ideal transformer

## Slide 42
Ideal transformer model in per unit: voltages
Ideal transformer

## Slide 43
Ideal transformer model in per unit: currents
and
and
=
Ideal transformer

## Slide 44
Ideal transformer model in per unit: impedances
Ideal transformer

## Slide 45
Ideal transformer model in per unit
If we express voltages and currents in per unit,
it is as if the ideal transformer was not there!
Impedances in per unit have the same value,
whether from the primary or secondary side

## Slide 46
Actual transformer model
Ideal transformer

## Slide 47
Actual transformer model in per unit

## Slide 48
Simplified transformer model

## Slide 49
Simplified transformer model

## Slide 50
Three-phase transformer: Y-Y connection
A
B
C
N
a
b
c
n
A
B
C
N
n
a
b
c

## Slide 51
Three-phase transformer: Y- connection
A
B
C
N
a
b
c
a
b
c
A
B
C
N

## Slide 52
Three-phase transformer: - connection
A
B
C
a
b
c
a
b
c
A
B
C

## Slide 53
Three-phase transformer
Magnetic core

## Slide 54
Transformer rating
Primary voltage rating and secondary voltage rating
  Define transformer ratio
  Lower voltages are fine
  Slight overvoltages are OK but larger overvoltage could damage insulation
MVA rating
  Determines how much power the transformer can carry
  The issue is the losses in the transformer
  Primary and secondary current ratings
  The transformer does not care whether it is active or reactive power. What matters is the current flowing through.

## Slide 55
Example 7.5
A three-phase Y-Y 13.8kV/416V transformer is rated at 12 kVA.
Calculate the maximum primary and secondary currents.

## Slide 56
Example 7.6
Generator: 75 MVA, 11 kV, =1.83 p.u.
Step-up transformer T1: -Y, 75 MVA, 11 kV/132 kV, ,
Line: 20 km long with
Step-down transformer T2: Y-, 45 MVA, 132 kV/33 kV, ,
Load: 10 MVA at 0.8 p.f. lagging. Nominal voltage magnitude at the load.
G
T1 : 11kV/132kV
T2: 132 kV/33kV
Line
Load


## Slide 57
Example 7.6
G
T1 : 11kV/132kV
T2: 132 kV/33kV
Line
Load
Load

## Slide 58
Example 7.6
Load

## Slide 59
Tap-changing transformer
Mechanical arm
Fixed N1
Variable N2
 Adjustable transformation ratio
 Useful for voltage regulation

## Slide 60
Regulating the voltage with a tap changing transformers
Voltage magnitude on the transmission network varies
Distribution utility must keep the voltage magnitude at the consumers’ premises within a narrow range
Adjust the taps to keep the magnitude on the low voltage side roughly constant
Due to the impedance of the feeder, the voltage at the end of the feeder is lower than at the source
Transmission
Network
Step down
tap-changing transformer
Distribution Feeder
Consumer loads

## Slide 61
On-load tap changing transformer (OLTC)
On-load means that the current is not interrupted as the position of the tap is adjusted
Slow acting regulation to reduce the number of adjustments and hence the need for maintenance
Transmission
Network
Distribution Feeder
Consumer loads
Tap changing mechanism
+
-

## Slide 62
Modeling tap-changing transformers
Per unit system:  ideal transformer disappears
In a tap changing transformer, the turns ratio is no longer constant
Let
 voltage boost on secondary side
 voltage buck on secondary side
N1
N2

## Slide 63
Modeling tap-changing transformers
Express quantities in per unit  remove N1/ N2 ideal transformer
Must retain 1:t off-nominal ideal transformer
How does that affect the transformer impedance?
Neglect shunt branches and put impedance on secondary side
N1
N2
Ideal transformer
SI units
Per Unit

## Slide 64
Modeling tap-changing transformers
Develop a -equivalent model?
Ideal transformer

## Slide 65
Modeling tap-changing transformers
Ideal transformer

## Slide 66
Modeling tap-changing transformers
Ideal transformer

## Slide 67
Modeling tap-changing transformers

## Slide 68
Modeling tap-changing transformers
Convert to impedances
with

## Slide 69
Boost voltage on secondary side:
Injects reactive power on secondary side
Absorbs reactive power on primary side

## Slide 70
Buck voltage on secondary side:
Absorbs reactive power on the secondary side
Injects reactive power on the primary side

## Slide 71
Load
The source maintains nominal voltage at its terminals and the load is modeled as a resistance in parallel with an inductive reactance When on its nominal tap position, the transformer is modeled as an inductive reactance
Calculate the voltages and powers when the and
Example 7.7: Tap changing transformer

## Slide 72
Load
Example 7.7: Tap changing transformer

## Slide 73
Load
Example 7.7: Tap changing transformer

## Slide 74
Phase-shifting transformer
a
b
c
A
B
C
Shunt transformer
Series transformer

## Slide 75
Phase-shifting transformer
Ideal phase-shifting transformer
Complex tap ratio

## Slide 76
Modeling a phase-shifting transformer
Ideal transformer same complex power on both sides

KVL on secondary side:
No physical model
Ideal phase-shifting transformer

## Slide 77
Phase-shifting transformer
Introduces a controllable phase shift between the primary and secondary
Useful for controlling active power flow
Relatively rare because quite expensive

## Slide 78
Switchgear
Various types of mechanical switching devices
Connect a component in service
Disconnect a component
Connect a component to ground for safety
Disconnect a faulted component
Alter flows in the network

## Slide 79
Interrupting a current
Voltage across the switch upon opening:
Arc = ionization of the air
Must be extinguished before it destroys the switch!
  Rapid separation of the contacts
  Cooling the arc with a blast of air
  Use vacuum or SF6
Very large!

## Slide 80
Types of switchgear
Circuit breaker
  Can interrupt a fault current
Disconnect switches
  Cannot interrupt a current
Combination
Circuit breaker
Disconnect switches

## Slide 81
Circuit breaker and disconnect switch

## Slide 82
Reactive compensation devices
Mechanically-switched capacitors
Mechanically-switched inductors
Help balance reactive power in the system
Coarse control of voltages
Finer control using electronically-controlled devices
  Static VAr Compensator (SVC)
Connected in shunt

## Slide 83
Shunt capacitor banks
Source: Eaton
Distribution level capacitor bank
Transmission level capacitor bank
Source: GE Grid Solutions

## Slide 84
Shunt reactor (inductor) bank
Source: Electrical Engineering Portal

## Slide 85
Static VAr Compensator
Source: GE Grid Solutions

## Slide 86
Busbar
Source: justanswer.com
Source: wikipedia
A busbar is a piece of conducting material where switches, lines, transformer and other devices are connected. In a three-phase system, a busbar consists of three such pieces of conducting material.

## Slide 87
Substations
Locations where lines and transformers are connected
Contains:
  Switchgear
  Busbars
  Transformers
  Reactive compensation devices
Various configurations
  Tradeoff between reliability/flexibility and cost
Reliability: avoid/minimize customer outages in case of fault
Flexibility: ability to do maintenance without outages

## Slide 88
Single busbar substation
Simplest configuration
Inflexible
  Maintenance requires outage
Poor reliability
  Everything is disconnected in the event of a busbar fault
Used only at the interface between transmission and distribution
Line 1
Line 2
T 1
T 2
Disconnect
Breaker
Busbar

## Slide 89
Ring bus
More flexible
  Breakers can be maintained without outages
Higher reliability
Higher flexibility
Higher cost
Line 1
Line 2
Load 1
Load 2

## Slide 90
Breaker-and-a-half substation
1.5 breaker per component
  Line, transformer, generator
Highest flexibility and reliability
Highest cost
Requires a larger area
G
G
Line 1
Line 2
Line 3
Busbar 1
Busbar 2
Load 1

## Slide 91
Busbar vs. bus
A bus is a set of busbars connected by closed switches.
A bus is equivalent to an electrical node
A busbar is a physical device
A bus is:
  An abstract concept
  Dynamic
The number of buses in a substation varies depending on the position of the switches
Two components separated by an impedance are not on the same bus
G
G
Line 1
Line 2
Line 3
: open circuit breaker
: closed circuit breaker

## Slide 92
How many buses in this substation?
G
G
Line 1
Line 2
Line 3
Bus 2
Bus 1
Bus 3
Bus 4
Bus 5
: open circuit breaker
: closed circuit breaker