## Slide 1: Chapter 11: Introduction to Power System Stability

## Slide 2: On a good day for a power system
Things change over time
But things change as expected:
  Load follows the forecast reasonably well
  Generators come online as expected
  Changes in network topology occur in a controlled manner
  All variables remain within expected limits
  No unexpected outages of generators or network components
  No faults
System is in quasi-steady state
Study its evolution using the algebraic power flow equations
  As opposed to differential equations

## Slide 3: What can go wrong?
Fault on a line, transformer, or busbar
Generator failure
Unexpected rapid decrease in renewable production
Unexpected rapid increase in load

## Slide 4: What usually happens after such a contingency?
System is designed and operated with a sufficient safety margin
System state moves to another stable operating point
Operators take action to restore the safety margin
System ready to handle another contingency
(That’s why we don’t have movies about engineers…)

## Slide 5: What else can happen?
Contingency is beyond the design and operation criteria
  Severe storm causes the disconnection of multiple lines at the same time
Contingency is compounded by a human error
  Mistake in operational planning
  Mistake in operation
  Example: cruise ship incident in Europe
  The process is usually to blame, not the individual
Contingency is compounded by a protection failure
  Fault is not cleared in a timely manner
  More components than necessary are disconnected

## Slide 6: What then?
System may go unstable
Protection system disconnects more equipment
Cascading outages
  e.g., cruise ship incident
Can lead to a partial or complete system collapse: blackout
  Partial collapse:
    The opening of circuit breakers isolates the part of the system that collapses
    If the load/generation balance can be maintained, the rest of the system, does not collapse

## Slide 7: Equilibrium
Equilibrium state:
  The state of the system won’t change except due to an external perturbation
Solving the power flow equations
   Equilibrium state of the power system for given loads and generations
Change in loads or generation change
   The equilibrium state of the power system changes
Is this equilibrium stable?

## Slide 8: What makes a system stable?
x
(state variable describing the system)
Potential energy
System State

## Slide 9: Stable System
x
Potential energy
Perturbation
Return to equilibrium state

## Slide 10: Unstable System
x
Potential energy
Equilibrium state

## Slide 11: Unstable System
x
Potential energy
Perturbation
This equilibrium is unstable!

## Slide 12: Slow Evolution of a Stable System
x
Potential energy
Original conditions
New conditions

## Slide 13: Steady State Stability
x
Potential energy
Instability!
The system has evolved to a state where it does not return to its equilibrium point after a small perturbation

## Slide 14: Transient Stability
x
Potential energy

## Slide 15: Transient Stability
x
Potential energy
Large
perturbation
How large a perturbation would be
Needed to make the system unstable?
Is the stability margin large enough
to withstand a large perturbation?
Stability margin

## Slide 16: Steady state stability vs. transient stability
Steady state stability is a function only of the system and its state
Transient stability depends not only on the system and its state but also on the size of the perturbation
Any system is unstable if the perturbation is sufficiently large…
Must limit the analysis to “credible” perturbations

## Slide 17: Stability limits
Steady state stability:
  Will the system collapse if a line or generator is disconnected?
Transient stability:
  Will a fault kick the system into instability?

## Slide 18: PV Curves
constant
Line modeled as pure reactance

## Slide 19: PV Curves

## Slide 20: PV Curves – Unity power factor load (
Chart: 
Chart: 
and
No solution for !
(a.k.a. “Nose Curves”)

## Slide 21: PV Curves – Lagging power factor load (
Chart: 
and
Voltage drops faster as
Maximum is smaller
pf = 1.0
pf = 0.9 lag

## Slide 22: PV Curves – Leading power factor load (
Chart: 
and
Voltage initially increases as
Maximum is larger and happens for a larger
pf = 1.0
pf = 0.9 lag

## Slide 23: Maximum active load
Chart: 
Chart: 
The two solutions coincide

## Slide 24: Maximum active load
The two solutions coincide when

## Slide 25: Example 11.1
Maximum load that this system can deliver for load power factors of 1.0, 0.9 lag, and 0.9 lead?

## Slide 26: Example 11.1
Power factor |  |  | 
Unity | 0 | 1.6667 | 0.7071
0.9 lag |  | 1.0446 | 0.5901
0.9 lead |  | 2.6591 | 0.9415
Power factor |  |  | 
Unity | 0 | 1.6667 | 0.7071
0.9 lag |  | 1.0446 | 0.5901
0.9 lead |  | 2.6591 | 0.9415
Less than the 0.95 p.u. that is
usually considered acceptable
Practical maximum loading is smaller than critical load

## Slide 27: Example 11.2
Practical loading limit?
Unity power factor ( ):
of critical load

## Slide 28: Example 11.3
System operates at maximum practical limit ()
One of the lines is disconnected
 Impedance between source and load increases

## Slide 29: Example 11.3
Two lines
One line
To avoid a system collapse if one of the lines were to be disconnected, the loading must be less than the critical value with only one line in service

## Slide 30: Example 11.4
Both lines are in service
Unity power factor using reactive power compensation
Well below critical loading
Reactive power compensation fails  0.9 p.f. lag

## Slide 31: Example 11.4
Unity pf
0.9 pf lag
A
B
Unacceptably low voltage
Dangerously close to critical load

## Slide 32: Cascading overloads
A
B
100 MW
100 MW
100 MW
Each line is rated at 140 MVA
System A is exporting 300 MW to system B

## Slide 33: Cascading overloads
A
B
100 MW
100 MW
100 MW
Each line is rated at 140 MVA

## Slide 34: Cascading overloads
150 MW
150 MW
Remaining lines are overloaded
Unless generation in system B is rapidly increased, they will trip
A
B

## Slide 35: Cascading overloads
What happens if the systems separate, and no action is taken?
Excess generation in system A  frequency increases
 generators trip on overspeed
Deficit of generation in system B  frequency decreases
 generators trip on underfrequency
A
B

## Slide 36: Example 11.5
Generator A is cheaper than generator B
Want to generate as much as possible with generator A
Must avoid the risk of cascading overload
Can’t rely on fast response from the generators
How much can generator A produce?
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 

## Slide 37: Example 11.5
Will the disconnection of one of the lines overload the remaining ones?
Need to perform a contingency analysis
How does distributes itself among the remaining lines?
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 

## Slide 38: Parallel paths – Power divider
P
P
Analog to current divider
Path A
Path B
Notes: Fig. 6.2: Illustration of Kirchoff’s Voltage Law

## Slide 39: Example 11.5
Contingency 1: disconnection of line 1
Flow through line 2:
Flow through line 3:
We must have
We must also have
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
 less constraining

## Slide 40: Example 11.5
Contingency 2: disconnection of line 2
Similar to contingency 1
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 

## Slide 41: Example 11.5
Contingency 3: disconnection of line 3
Flow through line 1:
Flow through line 2:
We must have
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
 less constraining

## Slide 42: Example 11.5
The most severe contingency is thus the disconnection of line 1 or line 2
To avoid overloading line 3 if this contingency were to occur, we must have
Hence
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 
Line | Rating | Impedance
1 | 50 MVA | 
2 | 50 MVA | 
3 | 40 MVA | 

## Slide 43
European incident of 4 November 2006

## Slide 44: European incident of 4 November 2006
Line disconnected to let the ship pass safely
Other lines disconnected

## Slide 45
European incident of 4 November 2006
Source: UCTE

## Slide 46: Frequency in the three areas following the separation
Source: UCTE

## Slide 47: Electromechanical stability
Commonly known as transient stability
Interactions between the mechanical and electrical systems
Mechanical system: rotating generators providing power
Electrical system: export power from the generator to the loads
These systems are coupled
How does this electromechanical system respond to a fault?

## Slide 48: Mechanical model of synchronous generators
angular position of the rotor
Newton’s law of motion :
moment of inertia of prime mover and generator
Prime Mover
Grid

## Slide 49: Synchronous generator in the steady state
 Synchronous speed
Prime Mover
Grid

## Slide 50: Deviations from synchronous speed
 Angular deviation from synchronous reference
Prime Mover
Grid

## Slide 51: Deviations from synchronous speed

Prime Mover
Grid

## Slide 52: Swing equation
Prime Mover
Grid

## Slide 53: Swing equation
: power in per unit
: MVA rating of the generator
Prime Mover
Grid

## Slide 54: Introducing the inertia constant
The moments of inertia of generators vary over a wide range  inconvenient
Inertia constant of a generator:
Ratio of the kinetic energy at synchronous speed to the MVA rating of the generator:

## Slide 55: Electrical vs. mechanical angles
One mechanical rotation of a generator with poles produces periods of the electrical output
Electrical angles
Mechanical angles

## Slide 56: Swing equation in electrical angles

## Slide 57: Final form of the swing equation
Swing equation as a second-degree differential equation

## Slide 58: Swing equation as first order differential equations
More convenient for simulation using numerical integration

## Slide 59: Example 11.6
Generator in the steady state and operating at synchronous speed
Bolted three-phase faults at its terminals at
 for
remains unchanged for the time interval considered
How does the angle change over time?
Grid
Prime Mover

## Slide 60: Example 11.6
For simplicity, we will assume that
with the initial condition
is determined by the pre-fault loading of the generator

## Slide 61: Example 11.6
How much would it require for a 60 Hz generator with an inertia constant operating at rated power and a rotor angle to reach following such a fault?

## Slide 62: Example 11.6
60 Hz generator 
Rated power 
 for


A small change in speed results in a
significant change in the angle

## Slide 63: Electrical model of synchronous generators
Electrical dynamics of generators are very complex
A detailed analysis of these dynamics is outside the scope of this course
We will limit our analysis to the simplified, “classical” model

## Slide 64: Subtransient, transient and synchronous reactances
Subtransient state
Subtransient reactance
Transient state
Transient reactance
Steady state
Synchronous reactance

## Slide 65: Subtransient, transient and steady periods
Subtransient state
Valid for a few 10’s ms
Transient state
Valid for a few 100’s ms
Steady state
Compatible with mechanical transients

## Slide 66: The classical dynamic model of generators
Same structure as the steady-state model
Synchronous reactance replaced by transient reactance
is a valid approximation during the electromechanical transients

## Slide 67: The classical dynamic model of generators
Generator unloaded:
  
Generator loaded:
, : voltage induced in the stator by rotor magnetic field
thus represents the position of the rotor
is thus the same angle as in the mechanical model

## Slide 68: Connecting the mechanical and electrical models
Electrical and mechanical angle
Electrical power

## Slide 69: Modeling the rest of the system
Stability is a characteristic of the entire system
Must connect the electromechanical model of the generator to a model of the rest of the system
Simplest model of the rest of the system: infinite bus beyond a reactance
Infinite bus = ideal voltage source
  Constant voltage magnitude
  Constant frequency
  Constant phase angle
Simplistic but useful to understand what affects stability
We’ll consider more realistic models later

## Slide 70
One-machine vs. infinite bus model
Transmission network
Rest of the system
Generator under study

## Slide 71
Electric power in the one-machine vs. infinite bus model

## Slide 72: Stable and unstable operating points
Chart: 
Steady state:
Operating point S at
What about operating point U at ?
(degrees)
S
U

## Slide 73: Small disturbances around the operating points
Chart: 
(degrees)
S
U
S1
S2
U2
U1

## Slide 74: Stable and unstable operating points
Chart: 
Any point S with is a stable operating point
Any point U with is an unstable operating point
Valid only for small disturbances
(degrees)
S
U

## Slide 75: Steady state stability limit
Chart: 
(degrees)
Steady state stability limit
Normal operating zone
Generators are normally operated with because a large disturbance (i.e., a fault ) could cause an instability

## Slide 76: Example 11.7
A synchronous generator with a transient reactance delivers apparent power at 0.95 pf lagging and nominal voltage.
Calculate the rotor angles corresponding to the stable and unstable operating points.
Chart: 
(degrees)
S
U

## Slide 77: Example 11.7
A synchronous generator with a transient reactance delivers apparent power at 0.95 pf lagging and nominal voltage.
Calculate the rotor angles corresponding to the stable and unstable operating points.
Chart: 
Chart: 
(degrees)
S
U
Hence:
.
By symmetry:

## Slide 78: Simplest example of large disturbances
Generator injects power into the infinite bus through a single line of reactance
Bolted three-phase fault immediately to the right of
Fault cleared by opening of
Effect on the electromechanical dynamics of the generator?
assumed constant

## Slide 79: Simplest example of large disturbances
Pre-fault conditions:
  Gives the initial value of for the differential equations
Fault conditions:
Post-fault conditions

## Slide 80: Simplest example of large disturbance
Chart: 
D
(degrees)
S
U
B
C
A
Momentum
Momentum (kinetic energy) is exhausted
Back towards the stable operating point

## Slide 81: Simplest example of large disturbance
Chart: 
(degrees)
S
U
B
C
A
Momentum
Kinetic energy not exhausted before reaching the unstable operating point
Angle continues to increase  instability

## Slide 82: Marble Analogy
Marble is released
Gravity causes the marble to accelerate

## Slide 83: Marble Analogy
Marble reaches the bottom
Acceleration becomes negative because it goes uphill
Marble does not stop because it has acquired momentum

## Slide 84: Marble Analogy – Stable case
Marble has exhausted its momentum before reaching top of the next hill
Speed is zero
Marble starts moving downwards because of gravity

## Slide 85: Marble Analogy – Stable case
Marble settles at the bottom when friction (damping) has consumed all the kinetic energy acquired during the initial downhill
Note that our simple power system model does not include damping

## Slide 86: Marble Analogy – Unstable case
Marble still has some momentum when it reaches the top of the next hill
Marble starts accelerating again
Instability

## Slide 87: Simplest example of large disturbance
Chart: 
(degrees)
S
U
A
B
C
D
System remains stable if

## Slide 88: Equal area criterion
Generator speeds up during the fault
 It acquires kinetic energy during the fault
Generator slows down after the fault is cleared
 It injects this kinetic energy back into the system
Can it return enough kinetic energy (i.e., slow down) before it reaches the unstable equilibrium point?
Develop a simple criteria
Visualize the factors that influence stability

## Slide 89: Equal area criterion
Swing equation:
Assume
Justification: a small increase in speed result in a large change in the angle
Simplified version:
Integrate between two arbitrary angles :

## Slide 90: Measuring kinetic energy
Swap and and integrate over rather than :
, : speeds of the generator when it is at angles and
Observe that

## Slide 91: Measuring kinetic energy
Change in kinetic energy
Change in kinetic energy
represents a change in kinetic energy

## Slide 92: represents a change in kinetic energy
Chart: 
(degrees)
S
U
Kinetic energy acquired during the fault ()
Kinetic energy returned to the grid after the fault
Is cleared ()

## Slide 93: Stability criterion
Chart: 
(degrees)
S
U
System will remain stable if the generator can return this kinetic energy to the grid before reaching the unstable equilibrium point U.
Mathematically: .

## Slide 94: Critical clearing angle
Chart: 
(degrees)
S
U
such that ?

## Slide 95: Calculating the critical clearing angle
Chart: 
is such that:
Equivalent to:
(degrees)
S
U

## Slide 96: Calculating the critical clearing angle

## Slide 97: Example 11.8
for each line


## Slide 98: This case is informative but not realistic…
Before the fault, the generator injects power through one line of reactance
During the fault, the generator injects no power at all
After the fault, the generator injects power through the same line of reactance
In other words, the system is back to its original state
This is usually not the case
Let us develop some more sophisticated examples

## Slide 99: A somewhat more realistic scenario
Pre-fault
Fault
Post-fault

## Slide 100: Power angle curves for this scenario
Chart: 
(degrees)
C
F
E
D
U
A
B

## Slide 101: Example 11.9
for each line
and

## Slide 102: Example 11.10
for each line

## Slide 103: Example 11.10
Pre-fault
Fault
Post-fault

## Slide 104: Example 11.10 – Fault conditions
Replace by Thevenin equivalent

## Slide 105: Example 11.10
Pre-fault
Fault
Post-fault

## Slide 106: Example 11.10

## Slide 107: Example 11.10
Chart: 
A
(degrees)
B
C
U
D
E
F

## Slide 108: Example 11.10
for :
Chart: 
Chart: 
A
(degrees)
B
C
U
D
E
F

## Slide 109: What factors affect stability?
Chart: 
A
What decreases ?
What increases ?
(degrees)
B
C
U
D
E
F

## Slide 110: What factors affect stability?
Chart: 
A
Faster relaying and circuit breakers
Reduces
Increases
Limitation?
  Extinguishing an arc is not easy
(degrees)
B
C
U
D
E
F

## Slide 111: What factors affect stability?
Chart: 
A
Increase inertia
Reduces
Increases
Limitation?
  Adding unnecessary steel is expensive
Inverter-based generation (wind, solar) don’t contribute to inertia
(degrees)
B
C
U
D
E
F

## Slide 112: What factors affect stability?
Chart: 
A
Reduce and
Reduces
Increases
Limitations?
  Decreases production from cheaper generating units
  Increases production from more expensive generating units
(degrees)
B
C
U
D
E
F

## Slide 113: What factors affect stability?
Chart: 
A
Decrease pre- and post-fault
Reduces
Increases
(degrees)
B
C
U
D
E
F

## Slide 114: What can be done to improve stability?
Limit pre-fault power injected by the generators
Limits depends on the operational conditions
  Lines that are in service
  Other generation
Affects the cost of producing power
System should be designed to allow generators to produce their rated power under normal conditions

## Slide 115: What can be done to improve stability?
Reduce reactance between generation and load
  Locate generation closer to the load
  Build parallel lines or parallel paths between generation and load
  Build higher voltage lines
     per unit impedance decreases with the square of the voltage
  Series compensation

## Slide 116: Series compensated line
Intrinsic resistance and inductance of the line
Intrinsic susceptance of the line
Series compensation

## Slide 117: Series compensation equipment

## Slide 118: Problems with series compensation
Protection of series compensated lines is difficult
Risk of subsynchronous resonance
  Resonance frequency of an LC circuit:
  Can match the torsional resonance frequency of turbogenerators
Creates torsional oscillations in these turbogenerators
Leads to metal fatigue and failure of the shaft

## Slide 119: High Voltage DC Transmission
DC does not introduce stability issues
Power transfer controlled using power electronics
Ideal for transmitting large amounts of power over long distances

## Slide 120: Existing and planned HVDC lines
Source: Iowa State University
Blue: Existing links
Red: Proposals

## Slide 121: Transient stability analysis using time domain simulation
Equal area criterion
  Provides useful insights on what affects stability
  Applicable only to simple cases
  Inaccurate
Need a more rigorous method for assessing stability
  More accurate results
  Applicable to multi-machine systems
Numerical integration of the differential equations

## Slide 122: What is a differential equation?
Given:
We want to calculate

## Slide 123: Numerical integration of differential equations
Given a value of , we can calculate the derivative of
We know that
We can calculate
This gives us the tangent to at

## Slide 124: Numerical integration of differential equations
For a sufficiently small timestep , the tangent is a good approximation of the function

## Slide 125: Step-by-step integration using Euler’s formula
Replace the function by a piecewise linear approximation
…

## Slide 126: Example 11.11
Analytical solution:
Error increases progressively
0 | 0 | 2.0 | 1.0 | 1.0
1 | 0.01 | 2.04 | 1.02 | 1.02020134
2 | 0.02 | 2.0808 | 1.0404 | 1.04081077
3 | 0.03 | 2.122416 | 1.061208 | 1.06183655
4 | 0.04 | 2.16486432 | 1.08243216 | 1.08328707
5 | 0.05 | 2.20816161 | 1.10408080 | 1.10517092
6 | 0.06 | 2.25232484 | 1.12616242 | 1.12749685
7 | 0.07 | 2.29737134 | 1.14868567 | 1.15027380
8 | 0.08 | 2.34331876 | 1.17165938 | 1.17351087
9 | 0.09 | 2.39018514 | 1.19509257 | 1.19721736
10 | 0.1 | 2.43798884 | 1.21899442 | 1.22140276
0 | 0 | 2.0 | 1.0 | 1.0
1 | 0.01 | 2.04 | 1.02 | 1.02020134
2 | 0.02 | 2.0808 | 1.0404 | 1.04081077
3 | 0.03 | 2.122416 | 1.061208 | 1.06183655
4 | 0.04 | 2.16486432 | 1.08243216 | 1.08328707
5 | 0.05 | 2.20816161 | 1.10408080 | 1.10517092
6 | 0.06 | 2.25232484 | 1.12616242 | 1.12749685
7 | 0.07 | 2.29737134 | 1.14868567 | 1.15027380
8 | 0.08 | 2.34331876 | 1.17165938 | 1.17351087
9 | 0.09 | 2.39018514 | 1.19509257 | 1.19721736
10 | 0.1 | 2.43798884 | 1.21899442 | 1.22140276

## Slide 127: Limitations of Euler’s method
The time step must be very small for the numerical solution to remain close to the actual solution
  Accuracy: small difference at each step
  Stability: numerical solution deviates completely from the actual solution
The smaller the time step, the longer it takes to calculate the solution
Euler’s method is simple but inaccurate and not very stable

## Slide 128: Other numerical integration methods
Higher order methods
  Use data from more than one previous step
Predictor-corrector methods
  Refines the estimate of the derivative
  Example: modified Euler’s method
Variable step methods
  Adjust the step size as a function of the dynamics
    Rapid changes  smaller step size
    Slower changes  longer step size

## Slide 129: Numerical integration of the swing equation
Euler’s formula:
First order form of the swing equation:
Initial conditions:

## Slide 130: Numerical integration: pre-fault
Pre-fault conditions:

## Slide 131: Numerical integration: fault
Fault conditions:
Speed increases
Angle increases

## Slide 132: Numerical integration: post-fault
Post-fault conditions:
Speed decreases
Angle increases until
and then decreases unless exceeds

## Slide 133: Example 11.12: Simulation of Example 11.10
Time-domain simulations of the system of Example 11.10
Euler’s method with a time step
Fault onset at
Three different fault clearing times:
   Stable
   gets very close to the value of
   exceeds at about
Stable case oscillates because our model does not include damping (i.e., losses)

## Slide 134: Example 11.12: Simulation of Example 11.10
Chart: 
Chart: 
Unstable
Marginally stable
Stable
Re-acceleration beyond the unstable operating point
Fault cleared for the stable case
Onset of the fault
Fault cleared for the marginally stable and unstable cases
(degrees)
Time (s)

## Slide 135: Example 11.13 : Effect of generator loading
Time-domain simulations of the system of Example 11.10
Euler’s method with a time step
Fault onset at and cleared at
Three cases:
   Stable
   Marginally stable
   Unstable

## Slide 136: Example 11.13: Effect of generator loading
Chart: 
Chart: 
Unstable
Marginally stable
Stable
Fault
cleared
Onset of
the fault
(degrees)
Time (s)

## Slide 137: Dynamics of multi-machine systems
Assumption so far:
  One machine vs. infinite bus
  Fault affects only one generator
  Rest of the system in unaffected
In fact, faults affect all generators in the system
  Faults change the amount of electric power they inject in the network
  This changes the flows in the transmission lines
Transients of each generator affect the other generators
Must simulate these interactions

## Slide 138: Dynamics of multi-machine systems
System with generators
Each generator represented by the classical model:
  Constant voltage behind transient reactance
Transmission Network
and Loads

## Slide 139: Dynamics of multi-machine systems
For each generator :
 first order differential equations
is a function not only of but of the state of the entire system
Transmission Network
and Loads

## Slide 140: Initialization: Generators’ internal emf
Perform a power flow
Generator is connected to bus injects

## Slide 141: Initialization: Model loads as admittances
Load at bus
Voltage at bus is

## Slide 142: Initialization: Build admittance matrix
Internal buses of generators numbered to
Other buses numbered to
Injected current only at internal generator buses
Transmission Network
and Loads

## Slide 143: Initialization: Build admittance matrix
: vector of internal emf of the generators
  Magnitudes assumed constant, angles variable
: vector of voltages at other buses
: vector of currents injected by the generators

## Slide 144: Reduced system
Only interested in angles
Transmission Network
and Loads

## Slide 145: Reduced system
Only interested in angles

## Slide 146: Admittance matrices
Study solid fault on linenext to bus
Pre-fault admittance matrix
  Build matrix with all lines in service
Faulted admittance matrix
  Voltage at bus is zero
  Bus is merged with ground
  Remove row and column from the matrix
  Admittances of other lines connected to node are now admittances to ground
Post-fault admittance matrix
  Remove linefrom pre-fault admittance matrix

## Slide 147: Reduced system

## Slide 148: Multi-machine system equations
For all generator :
With:

## Slide 149: Integrating the differential equations
Set
For all generators, set
For all generators, calculate initial
Set
If , exit
Calculate for each generator using the latest values of
  If ,
  If , calculate using the faulted admittances
  If , calculate using the post-fault admittances
calculate and using Euler’s method
Go to step 4

## Slide 150: Example 11.14

## Slide 151: Example 11.14: fault at and cleared at .
Chart: 
Chart: 
(degrees)
Time (s)

## Slide 152: Example 11.14: fault at and cleared at .
Chart: 
Chart: 
(degrees)
Time (s)

## Slide 153: Effect of damping
Deviation from synchronous speed  flux linking damper windings is not constant
Currents induced in damper windings create a torque that opposes the speed deviations
This torque dampens the oscillations

## Slide 154: Example 11.15: fault cleared at with
Chart: 
Chart: 
(degrees)
Time (s)

## Slide 155: Detailed dynamic models
We have used the classical generator model
  Constant emf behind transient reactance
This model is simple but does not accurately reflect the dynamic electrical behavior of generators
Include differential equations to reflect the electrical dynamics of generators
Very large system of coupled differential equations