## Slide 1
Chapter 6: Balancing Load and Generation

## Slide 2
Conservation of energy
System boundary

## Slide 3
Power balance

## Slide 4
Drawing the boundaries of the system
is always valid
Meaning of the terms depends on how we draw the boundaries of the system
Particularly important when considering the energy stored
System boundary

## Slide 5
Input boundary at the terminals of the generators
electrical loads
: electrical power injected by these generators
: losses in the network
: batteries in the network (: charging : discharging)
  (Energy stored in inductances and capacitances assumed essentially constant and negligible)
Loads
Network
Batteries
System boundary
Output boundary
Input boundary

## Slide 6
Input boundary at the shafts of the generators
electrical loads
: mechanical power provided by the prime mover
: losses in the network + losses in the generator
: batteries in the network + kinetic energy stored in the rotating generators
Loads
Network
Batteries
System boundary
Output boundary
Input boundary
Prime Mover
Prime Mover
Prime Mover
Shafts

## Slide 7
Kinetic energy stored in the rotating generators
set of all synchronous generators
moment of inertia of generator
square of the mechanical rotational speed of generator
is proportional to the grid frequency
A change in frequency results in a change in stored energy:

## Slide 8
Input boundary at the primary energy input to the prime mover
Electrical loads
: Primary energy input
: losses in the network + losses in the generator + losses in the prime mover
: batteries in the network + kinetic energy stored in the rotating generators + thermodynamic energy in the prime mover
Loads
Network
Batteries
System boundary
Output boundary
Input boundary
Prime Mover
Prime Mover
Prime Mover
Primary Energy
Primary Energy
Primary Energy

## Slide 9
Input boundary at the storage of primary energy
: losses in the network + losses in the generator + losses in the prime mover + losses in primary energy
: batteries in the network + kinetic energy stored in the rotating generators + thermodynamic energy in the prime mover + primary energy storage
Loads
Network
Batteries
System boundary
Output boundary
Input boundary
Prime Mover
Prime Mover
Prime Mover
Primary Energy
Primary Energy
Primary Energy

## Slide 10
Steady state
(neither charging nor discharging)
Steady state assumption is very useful when planning the operation of the system
Example:
  Forecast that the load + losses tomorrow at noon will be 1000 MW
  Must be prepared to generate 1000 MW

## Slide 11
Perturbation
Steady state:
Sudden increase in load:
  Generators cannot increase their output instantaneously
  We must still have:
  Therefore, we must have until we have:
  The amount of energy stored in the system decreases
Where this stored energy comes from depends on the time frame that we consider

## Slide 12
Time frames
First draw power from kinetic energy stored in generator-prime movers
Then draw power from thermodynamic energy stored in turbines
Then increase power input to prime mover (increase )
Loads
Network
Batteries
Prime Mover
Prime Mover
Prime Mover
Primary Energy
Primary Energy
Primary Energy

## Slide 13
Single generator
Mechanical power & torque
Electrical power & reaction torque
Newton’s law of motion
  : combined moment of inertia of the prime mover and the generator
Prime Mover
Load

## Slide 14
Single generator
Steady state:
frequency is constant
Load suddenly increase from
frequency decreases
Prime Mover
Load

## Slide 15
Governor control
Detects positive or negative difference between actual speed and reference speed
Adjusts the amount of primary energy injected in the prime mover
Restores the equilibrium:
Frequency is stabilized
Primary frequency control
Governor
Prime Mover
Primary energy
+
-
Load

## Slide 16
Droop characteristic
Primary frequency control does not maintain the frequency at its nominal value as the load changes
Aggregated load has a slight dependence on frequency
Load characteristic
Generator droop characteristic

## Slide 17
Example 6.1
The governor of a 50kW, 60 Hz generator has a droop of 4%. Calculate the frequency provided by this generator when it supplies a 25kW load. Neglect the frequency dependence of the load.

## Slide 18
Multiple generators
Network
Generators
Loads
: set of generators
: mechanical power of the prime mover of generator
: electrical power produced by the generator
: set of loads
: power consumed by load
power losses in the network and the generators
In the steady state:

## Slide 19
Multiple generators
Network
Generators
Loads
combined inertia of all the generators and their prime movers
 All the generators decelerate together
 System frequency decreases
Sudden increase in load:

## Slide 20
Multiple generators
Network
Generators
Loads
combined inertia of all the generators and their prime movers
 All the generators accelerate together
 System frequency increases
Sudden decrease in load:

## Slide 21
Multiple generators
Network
Generators
Loads
combined inertia of all the generators and their prime movers
 A sudden change in load has a much smaller effect in large systems than in small systems

## Slide 22
Multiple generators
Network
Generators
Loads
Changes in loads are usually gradual. Large changes in generation can be sudden
because of generator failures

## Slide 23
Multiple generators: Governor control
Any imbalance between generation and load causes the frequency to drop or rise
The governor of each generator reacts to this frequency change according to its droop characteristic
Network
Generators
Loads

## Slide 24
Load sharing between generators
Two generators with same
droop coefficient
These two generators share the load and operate at the same frequency
Frequency determined by the combined droop characteristic
Generators share the load in proportion
to their capacity

## Slide 25
System droop characteristic
Generator 1
Generator 2
Load characteristic
System

## Slide 26
Example 6.2
Two 60 Hz generators supply a load of 20 kW. The first generator is rated at 20 kW and the second at 30 kW. They have the same droop coefficient of 0.04. Calculate the power produced by each generator and the operating frequency.

## Slide 27
Why a droop characteristic?
Generator 1
Generator 2
Assume that the two generators try to keep the frequency exactly constant.
However, the frequencies that they measure would never be exactly the same.
As a result, they would fight, and the system would be unstable.

## Slide 28
Electronically-connected generators
Electronically-connected generators do not naturally contribute to the inertia of the system
This poses a challenge as the proportion of renewable generation increases
Special control systems are being developed so these generators can provide virtual inertia

## Slide 29
Secondary frequency control
Primary frequency control stops frequency from declining/increasing when there is an imbalance
What’s good about it?
  Fast
  Simple
  Distributed (no need for communication)
  Allocates imbalances in proportion to generator rating
What are its limitations?
  Does not restore frequency to its nominal value
  Does not allocate generation economically
Need for secondary frequency control

## Slide 30
Secondary frequency control
Adjusts up or down
Shifts the whole droop characteristic up or down
Restores the frequency to its nominal value
Can be used to re-allocate load among the generators
Governor
Prime Mover
Primary energy
+
-
Load

## Slide 31
Droop characteristics without secondary frequency control
Generator 1
Generator 2
System
Droop characteristics with secondary frequency control

## Slide 32
Secondary frequency control
Centralized control
Control center sends reference signal to each generator
Adjusts the to restore the frequency at its nominal value (e.g., 60 Hz)
At that point we have
Since we don’t know the value of the load, we control the frequency
Primary frequency control reacts fast to keep the frequency from changing uncontrollably
Secondary frequency control reacts more slowly to restore the frequency to its nominal value
We’ll see later how secondary frequency control implements economic dispatch

## Slide 33
Response to a large disturbance
Primary frequency control
Secondary frequency control
Starting of gas turbine
Frequency
Time
Inertial response
Frequency nadir

## Slide 34
Loss of 1200 MW in the GB system on 4/18/2022

## Slide 35
Loss of generation event in the Western US 11/26/2022

## Slide 36
Major incidents
What if generators do not react fast enough to a large imbalance?
Frequency continues to decrease
Operating generators at too low a speed will damage them
  Automatic disconnection
Last line of defense: under-frequency load shedding

## Slide 37
Underfrequency load shedding in WECC
Block | % of Load | Frequency
1 | 5.3 | 59.1
2 | 5.9 | 58.9
3 | 6.5 | 58.7
4 | 6.7 | 58.5
5 | 6.7 | 58.3
Each block of load must be shed within 14 cycles of the frequency dropping below the corresponding threshold
WECC: Western US interconnection

## Slide 38
Great Britain, 9 August 2019

## Slide 39
Consequences

## Slide 40
European incident of 4 November 2006

## Slide 41
European incident of 4 November 2006
Line disconnected to let the ship pass safely
Other lines disconnected

## Slide 42
European incident of 4 November 2006

## Slide 43
European incident of 4 November 2006
In the Eastern part of the system, because there was more generation than load, the frequency increased suddenly. This was corrected by reducing the output of the generators. After 45 minutes, the system was reconnected.

## Slide 44
European incident of 4 November 2006
In the Western part of the system, there was much more load than generation. The frequency dropped very fast. To prevent the system from collapsing, 15 million customers were disconnected automatically. Generation was increased to restore frequency to its normal value.
Automatic Load Shedding

## Slide 45
European incident of 4 November 2006
Country Load shed
Austria 1500 MW
Belgium 800 MW
France 5200 MW
Germany/E.ON Netz 400 MW
Germany/RWE TSO 2000 MW
Italy 1500 MW
Netherlands 400 MW
Portugal 500 MW
Spain 1050 MW

## Slide 46
Incident on DC interconnector between Norway and Germany

## Slide 47
Sudden reversal of power flow
Norway, Sweden, Finland went from importing 1200 MW to exporting 600 MW
This created a large load/generation imbalance

## Slide 48
Frequency on continental European system
Frequency on Scandinavian system

## Slide 49
Economic dispatch

## Slide 50
Goal of the economic dispatch problem
Given set of generating units are synchronized to the power system
How much power should each of these units produce to supply the load at minimum cost?
Minimize the cost of the fuel needed to produce this power
For wind and solar generation, this fuel cost is zero
Wind and solar generation are taken as given in the economic dispatch problem

## Slide 51
Heat rate curve of a thermal generating unit
Shows how much fuel must be burned each hour for the unit to produce a certain amount of power
Measured in the energy content of the fuel
MBTU: Million British Thermal Unit
Note the typical shape of the curve
Note the physical limits on the power production
(MBTU/h)

## Slide 52
Cost curve of a thermal generating unit
Multiply hourly fuel input by cost of fuel in $/MBTU
Extrapolation of the curve to usually leads to a value called the no-load cost
($/h)

## Slide 53
Mathematical formulation
Economic dispatch is a constrained optimization problem
Must define:
  Objective function
  Equality constraint

## Slide 54
Objective function
Minimize the cost of producing power with all the generating units
: set of generating units
: amount of power produced by unit
: hourly cost of producing with unit
The are the decision variables

## Slide 55
Equality constraint
Load/generation balance:
: load to be supplied by these generating units

## Slide 56
Solving this constrained optimization problem
Build the Lagrangian function of the problem:
Objective function
Equality constraint
Lagrange multiplier

## Slide 57
Optimality conditions
Set the partial derivatives of the Lagrangian function to zero
Partial derivatives with respect to the decision variables:
Derivative with respect to the Lagrange multiplier:
Solve these equations for the and

## Slide 58
Physical interpretation of the solution
At the optimum, all units operate at the same marginal cost

: cost of an extra MW from unit
At the optimum, a MW has the same cost from all generating units
Lagrange multiplier : cost of an extra MW at the optimum dispatch
: system marginal cost

## Slide 59
Visualisation of economic dispatch
If , reduce
If , increase

## Slide 60
Example 6.3: Economic dispatch
Cost functions of three generating units:
Load to be supplied at minimum cost by these three units:
Lagrangian function:

## Slide 61
Lagrangian function:
Partial derivatives:
Example 6.3: Optimality conditions




## Slide 62
Example 6.3: Solution for
 195.06 MW
 333.43 MW
 271.51 MW
 $/MWh

## Slide 63
Example 6.3: Solution for
 292.73 MW
 496.22 MW
 411.05 MW
 $/MWh  increases with the load

## Slide 64
Example 6.4: Economic dispatch and renewable generation
Same three thermal generating units:
Generation from a renewable source: 200 MW
Load
Net load to be supplied by the three thermal units:
Intermediate result of previous example:
$/MWh
146.22 MW; 252.03 MW; 201.74 MW

## Slide 65
Limits on generating units
Must compare the calculated against the upper and lower limit of each unit:
If all limits are satisfied  done
If a limit is violated  fix the corresponding at the limit and repeat the solution

## Slide 66
Example 6.5: Effect of generator limits on economic dispatch
Same thermal generating units as in Example 6.3
Limits on these units:
  MW
  MW
  MW
For , we calculated:
292.73 MW; 496.22 MW; 411.05MW; $/MWh
This is not a feasible solution
Set MW
to be supplied by units 1 and 3

## Slide 67
Example 6.5: Effect of generator limits on economic dispatch
Optimally dispatch with units 1 and 3
  $/MWh
  311. 76 MW
  438.24 MW
  $60,451.47
Calculate the marginal cost of each unit at this optimum;
All the units no longer operate at the same marginal cost
Producing more power with unit 2 would reduce the total cost but is not possible

## Slide 68
Example 6.6: Effect of generator limits on economic dispatch
Same thermal and renewable generating units as in Example 6.4
Limits on the thermal units:
  MW
  MW
  MW
In Example 6.4, for , we found:
146.22 MW; 252.03 MW; 201.74 MW
Infeasible solution
Set MW
to be supplied by units 2 and 3

## Slide 69
Example 6.6: Effect of generator limits on economic dispatch
Optimally dispatch with units 2 and 3
  $/MWh
  200 MW
  223.08 MW
  176.92 MW
Calculate the marginal cost of each unit at this optimum;
The marginal cost of unit 1 is higher than the system marginal cost because it is at its lower limit and cannot produce any less

## Slide 70
Economic dispatch with linear cost curves

## Slide 71
Visualisation of economic dispatch
If , reduce
If , increase

## Slide 72
Economic dispatch with linear cost curves

## Slide 73
Economic dispatch with linear cost curves

## Slide 74
Linear Cost Curves
The output of the unit with the lowest incremental cost (in this case unit A) is increased first (it is “loaded” first)
The output of the other units is not increased until unit A is loaded up to its maximum
The output of the unit with second lowest incremental cost is then increased (i.e. the “second cheapest” unit)
And so on until the generation meets the load

## Slide 75
Linear cost curves with minimum generation

## Slide 76
Linear cost curves with minimum generation
All generating units are first loaded up to their minimum generation
The generating units are then loaded in order of incremental cost

## Slide 77
Piecewise linear cost curves
Quadratic cost curves are convenient when solving ED problems by hand
Practical applications rely on piecewise linear cost curves
($/h)
($/h)

## Slide 78
Piecewise linear cost curves
Where:
: slope of the first segment
: slope of the second segment
: slope of the third segment
($/h)

## Slide 79
Example 6.7: Piecewise linear cost curves
MW
MW
MW
Arbitrary choice of elbow points , ,
 | Unit 1 | Unit 2 | Unit 3
(MW) | 200 | 200 | 200
(MW) | 300 | 300 | 300
(MW) | 400 | 420 | 420
(MW) | 500 | 450 | 500
($/h) | 7700 | 11000 | 10850
($/h) | 13500 | 14700 | 15250
($/h) | 21300 | 20724 | 22378
($/h) | 31100 | 22500 | 28250
($/MWh) | 58.00 | 37.00 | 44.00
($/MWh) | 78.00 | 50.20 | 59.40
($/MWh) | 98.00 | 59.20 | 73.40
 | Unit 1 | Unit 2 | Unit 3
 | 200 | 200 | 200
 | 300 | 300 | 300
 | 400 | 420 | 420
 | 500 | 450 | 500
 | 7700 | 11000 | 10850
 | 13500 | 14700 | 15250
 | 21300 | 20724 | 22378
 | 31100 | 22500 | 28250
 | 58.00 | 37.00 | 44.00
 | 78.00 | 50.20 | 59.40
 | 98.00 | 59.20 | 73.40

## Slide 80
Piecewise constant marginal cost curves
($/h)
($/MWh)

## Slide 81
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 82
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 83
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 84
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 85
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 86
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 87
Economic Dispatch with Piecewise Linear Cost Curves
PA
PB
PA
PB

## Slide 88
ED algorithm using piecewise linear cost curves
Input the cost curve data of all the generating units
Create a list of all the segments of the cost curves of all the generators
Order this list in increasing order of marginal cost
Set the power output of all the generators at their respective minimum value
Set the residual load at the actual load minus the sum of these minimum generations
Take the first or next segment in the list
If the length of this segment is less than the residual load:
  Increase the output of the corresponding generator by the length of this segment
  Decrease the residual load by the length of this segment
  Go to step 6
Else
  Increase the output of the corresponding generator by the residual load
  Exit.

## Slide 89
ED algorithm using piecewise linear cost curves
ED with this algorithm leads to a solution where:
All generators, except one, will be set at
  , or
  , or
  one of the elbow points
One generator operates somewhere along one of its segments
This generator would provide the next MW of load
This generator is called the marginal generator
The slope of this segment is the system marginal cost.

## Slide 90
Example 6.8: ED using piecewise linear cost curves
Segment number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Unit | 2 | 3 | 2 | 1 | 2 | 3 | 3 | 1 | 1
Segment length | 100 | 100 | 120 | 100 | 30 | 120 | 80 | 100 | 100
Marginal cost | 37.0 | 44.0 | 50.2 | 58.0 | 59.2 | 59.4 | 73.4 | 78.0 | 98.0
Table with ordered segments for the units of Example 6.7
Economic dispatch for a load of 800 MW
Residual load is thus 200 MW  covered by the first two segments in the list
Economic dispatch: 200.00 MW; 300.00 MW; 300.00 MW
Next MW of load would be provided by Unit 2 on its second segment
 the system marginal cost is 50.2 $/MWh
37,650 $/h

## Slide 91
Example 6.8: ED using piecewise linear cost curves
Segment number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Unit | 2 | 3 | 2 | 1 | 2 | 3 | 3 | 1 | 1
Segment length | 100 | 100 | 120 | 100 | 30 | 120 | 80 | 100 | 100
Marginal cost | 37.0 | 44.0 | 50.2 | 58.0 | 59.2 | 59.4 | 73.4 | 78.0 | 98.0
Table with ordered segments for the units of Example 6.7
Economic dispatch for a load of 1200 MW
Residual load is thus 600 MW  first six segments + 30 MW of seventh segment
Economic dispatch: 300.00 MW; 450.00 MW; 450.00 MW
System operates on the seventh segment  the system marginal cost is 73.4 $/MWh
Unit 3 is the marginal unit
60,580 $/h

## Slide 92
Load flexibility and storage
Conventional ED:
  Load is given
  Minimize cost by adjusting the output of the generators
Observation:
  Marginal cost increases significantly with the load
  A MW of load costs significantly more to produce when the load is high
Could reduce the overall cost by shifting loads from period of high loads to period of light loads
Use load flexibility and storage to achieve this

## Slide 93
Load flexibility
Due to the nature of the cost curves, the total cost increases more than linearly with the load
Shifting loads from periods of high demand to periods of low demand would thus reduce the total cost

## Slide 94
Example 6.9: Load shifting
What is the effect of shifting 50 MW from the 1200 MW load period to the 800 MW load period with the units of Example 6.8?
ED for an 850 MW load:
    200.00 MW; 350.00 MW; 300.00 MW
    40,160 $/h
ED for an 1150 MW load:
    300.00 MW; 450.00 MW; 400.00 MW
    57,190 $/h

## Slide 95
Example 6.10: Storage
What is the effect of storing 50 MWh during the low load period and releasing this energy during the high load period
Use the units of Example 6.8 and assume a storage roundtrip efficiency of 80%
Net load during the low load period: 800 + 50 = 850 MW
From Example 6.9: 40,160 $/h
Available energy from the battery: 40 MWh
Net load during the high load period: 1200 - 40 = 1160 MW
ED for 1160MW: 300.00 MW; 450.00 MW; 410 MW
Due to the efficiency of the storage, this is marginally profitable

## Slide 96
Unit Commitment (UC)

## Slide 97
Unit commitment
Periods of high load
   need more generating units
Periods of light load
   need fewer generating units

## Slide 98
Why unit commitment?
Questions:
  How many generating units do we need at any given time?
  Which set of units would be optimal?
  When should each unit be synchronized to the grid?
  When should each unit be de-synchronized from the grid?
Approach:
  Develop an intuitive understanding of the problem
  Formulate the unit commitment problem as a mathematical optimization problem

## Slide 99
Example 6.11: How many units?
Consider the generating units of Example 6.7
Perform an ED for each of the combinations of these units and a load of 475MW
Unit 1 (MW) | Unit 2 (MW) | Unit 3 (MW) | Total Cost ($) | Marginal Cost ($/MWh)
- | - | 475 | 26,415.00 | 73.4
- | X | - | Infeasible | -
475 | - | - | 28,650.00 | 98.0
- | 275 | 200 | 24,625.00 | 37.0
200 | 275 | - | 21,475.00 | 37.0
200 | - | 275 | 21,850.00 | 44.0
X | X | X | Infeasible | -
 Infeasible because load is larger than
 Impossible because
 Lowest cost

## Slide 100
Marginal cost vs. average cost
No-load cost
Variable cost
Marginal cost:
 Does not involve the no-load cost
Average cost:
 Does involve the no-load cost

## Slide 101
Optimal marginal and average costs as a function of the load
Chart: Load (MW)
| 600 | 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 1100 | 1150 | 1200 | 1250 | 1300 | 1350 | 1400 | 1450
Average cost | 49.1346 | 48.0769 | 47.4011 | 47.0308 | 46.9086 | 46.9827 | 47.1878 | 47.4998 | 47.9028 | 48.3836 | 48.9345 | 49.5972 | 50.3762 | 51.2576 | 52.2296 | 53.2821 | 54.4065 | 55.5953
Marginal cost | 33.7692 | 37 | 40.2308 | 43.4615 | 46.6923 | 49.4535 | 51.8953 | 54.3372 | 56.7791 | 59.2209 | 62.1176 | 66.2353 | 70.3529 | 74.4706 | 78.5882 | 82.7059 | 86.8235 | 90.9412
Minimum
Use fewer units to reduce
impact of no-load cost
Use more units to reduce
impact of marginal cost

## Slide 102
Total operating cost for different combinations of units
Chart: Load (MW)
| 200 | 200 | 300 | 300 | 300 | 300 | 420 | 500 | 500 | 500
Unit 3 only | 10850 | 10850 | 15250 | 15250 | 15250 | 15250 | 22378 | 28250 | 28250 | 28250
Unit 2 only | 11000 | 14700 | 14700 | 20724 | 20724 | 22500 | 22500 | 22500 | 22500 | 22500
Units 2 & 3 | 21850 | 25550 | 29950 | 35974 | 35974 | 37750 | 44878 | 50750 | 50750 | 50750
Unit 1 only | 7700 | 7700 | 7700 | 7700 | 13500 | 13500 | 13500 | 13500 | 21300 | 31100
Units 1 & 3 | 18550 | 18550 | 22950 | 22950 | 28750 | 28750 | 35878 | 41750 | 49550 | 59350
Units 1 & 2 | 18700 | 22400 | 22400 | 28424 | 34224 | 36000 | 36000 | 36000 | 43800 | 53600
Units 1, 2 & 3 | 29550 | 33250 | 37650 | 43674 | 49474 | 51250 | 58378 | 64250 | 72050 | 81850

## Slide 103
Setting up the unit commitment
Done daily for the next day
Forecast the load profile for the next day
Subtract from this forecast the expected generation from renewable sources
Discretize this net load forecast profile in hourly time intervals
Schedule the production of the conventional generating units to meet this profile at minimum cost

## Slide 104
Example of a 24-hour hourly net load forecast
Chart: Hour
| 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 4 | 5 | 5 | 6 | 6 | 7 | 7 | 8 | 8 | 9 | 9 | 10 | 10 | 11 | 11 | 12 | 12 | 13 | 13 | 14 | 14 | 15 | 15 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 20 | 20 | 21 | 21 | 22 | 22 | 23 | 23 | 24
 | 74780 | 74780 | 70985 | 70985 | 68020 | 68020 | 66545 | 66545 | 66102 | 66102 | 67529 | 67529 | 70522 | 70522 | 73820 | 73820 | 77746 | 77746 | 82226 | 82226 | 87228 | 87228 | 91579 | 91579 | 95493 | 95493 | 99325 | 99325 | 101421 | 101421 | 102937 | 102937 | 103834 | 103834 | 104313 | 104313 | 102699 | 102699 | 98764 | 98764 | 94966 | 94966 | 92594 | 92594 | 86739 | 86739 | 80399 | 80399

## Slide 105
Startup cost of thermal generating units
Thermal generating units must be “warmed up” before they can be synchronized
A certain amount of fuel must be burned to do this
Burning up this fuel costs money
 Startup cost
is incurred only when a unit is started
is not a function of the power produced
Production cost is a function of the power produced
Production cost includes the no-load cost
is incurred every hour unit is running
can be viewed as an investment in future power production

## Slide 106
Balancing startup and production costs
Thermal unit with large and low
  Example: large coal or nuclear unit
   Bring this unit online only if can be amortized over the production of a lot of power
Thermal unit with large and low
  Example: OCGT or diesel generator
  Bring this unit online if a small amount of power is needed for a short time
Scheduling cannot be done for each period separately
Scheduling must be done over a time horizon, typically one day

## Slide 107
Formulating UC as an optimization problem
Objective function:
: Set of available thermal generating units
: Set of hourly time intervals included in the horizon
: Status of unit
  if unit is generating (i.e. “on”) during period
  otherwise (i.e., “off”)
: Power produced by unit during period
: Startup cost of unit .
  Non-zero only if unit is turned on at time i.e., and
: Cost of producing for an hour with unit ,

## Slide 108
Formulating UC as an optimization problem
Load/generation balance constraint:
Constraints on the output of generating units:

## Slide 109
Formulating UC as an optimization problem
Ramp rate limits
To avoid potentially damaging temperature gradients in the turbine, changes in the power output must be limited between subsequent time intervals:

## Slide 110
Formulating UC as an optimization problem
Minimum up- and down-time constraints
For similar reasons, if a thermal generating units is turned on, it should remain on for a minimum time , and if it is turned off, it should remain off for a minimum number time :
The ramp rate and minimum up- and down-time constraints create a linkage between the optimization at different time intervals.

## Slide 111
Decision variables
Binary decision variables
  Status of unit (on or off) at every time interval
Continuous decision variables
  Power produced by unit at every time interval
Specify for all units and time interval  perform ED to find the
Theoretical optimum  must consider all combinations of
units  possible combinations of unit status at each time interval
time intervals  combinations

## Slide 112
Example 6.12: How many combinations?
Assessing one billion combinations per second would require years

## Slide 113
Solving the unit commitment problem
Assessing ALL combinations to find the optimal one is clearly impossible
UC is a mixed integer linear programming (MILP) problem
  are integer variables
  are continuous variables
Solve the ED using piecewise linear cost curves  linear programming
Use commercial-grade optimization software that implement ”branch and cut” algorithm to reduce the number of combinations that are considered
Provides a solution that is close enough to the optimal solution

## Slide 114
Example 6.13: Unit commitment
Example inspired by the documentation of the pypsa software tool
Load profile:
Parameters of generating units:
Single segment cost curves
Start by neglecting the no-load and startup costs
Hour | 1 | 2 | 3 | 4
Load (MW) | 4000 | 800 | 5000 | 3000
Unit Name | (MW) | (MW) | Marginal cost ($/MWh)
Hansel | 3,000 | 10,000 | 20
Gretel | 500 | 5,000 | 70
Unit Name |  |  | Marginal cost ($/MWh)
Hansel | 3,000 | 10,000 | 20
Gretel | 500 | 5,000 | 70

## Slide 115
Example 6.13: Unit commitment
Base case solution:
Since Hansel is much cheaper and has enough capacity, it carries the entire load during hours 1, 3 and 4.
However, the load at hour 2 is smaller than of Hansel
  Hansel must be shut down
  Gretel must be brought online
  At hour 3, Hansel is brought back online and Gretel is shutdown
Hour | 1 | 2 | 3 | 4
 | 4000 | 0 | 5000 | 3000
 | 0 | 800 | 0 | 0
Hour | 1 | 2 | 3 | 4
 | 4000 | 0 | 5000 | 3000
 | 0 | 800 | 0 | 0

## Slide 116
Example 6.13: Unit commitment
Effect of a minimum up-time of three hours for Gretel:
Effect of a minimum down-time of two hours for Hansel:
Hour | 1 | 2 | 3 | 4
 | 3500 | 0 | 4500 | 3000
 | 500 | 800 | 500 | 0
Hour | 1 | 2 | 3 | 4
 | 3500 | 0 | 4500 | 3000
 | 500 | 800 | 500 | 0
Hour | 1 | 2 | 3 | 4
 | 4000 | 800 | 500 | 0
 | 0 | 0 | 4500 | 3000
Hour | 1 | 2 | 3 | 4
 | 4000 | 800 | 500 | 0
 | 0 | 0 | 4500 | 3000

## Slide 117
Example 6.13: Unit commitment
Adding constraints:
  Changes the solution
  Increases the operating cost
 | Cost ($)
Base Case | 296000
Add min uptime | 346000
Add min down time | 521000

## Slide 118
Example 6.13: Unit commitment
Add a startup cost of $375,000 to to Hansel:
While Hansel is cheaper to run, it is not worth starting for such a short time
Hour | 1 | 2 | 3 | 4
 | 0 | 0 | 0 | 0
 | 4000 | 800 | 5000 | 3000
Hour | 1 | 2 | 3 | 4
 | 0 | 0 | 0 | 0
 | 4000 | 800 | 5000 | 3000

## Slide 119
Handling uncertainty
Sources of uncertainty:
  Load forecasting errors
    Typical error less than 2%
    Much larger errors can occur during unusual weather conditions
  Renewable generation
    Wind and solar generation can change rapidly with a weather front
  “Behind the meter” solar generation is not monitored by operators
  Large conventional generators can fail at any time
Operators need resources to handle uncertainty
Have generation capacity in reserve to handle load/generation imbalances

## Slide 120
Unit commitment with reserve
Headroom:
Total headroom must be larger than the reserve requirement:
Combine with load generation balance:
Reserve constraint:

## Slide 121
Reserve requirement
Must be able to handle the largest credible contingency
In a small system:
  Loss of largest committed unit
   = capacity of this unit
In a large system:
  Nearly simultaneous loss of multiple units or large decrease in renewable generation
   determined using probabilistic calculations
Committed generation must also be able to ramp up or down sufficiently fast
Including these constraints in UC often forces the commitment of additional units
  Increase in operating cost
Can also use voluntary load shedding or battery energy storage for reserve

## Slide 122
Example 6.14: Unit commitment with reserve
Unit Name | (MW) | (MW) | Marginal cost ($/MWh) | Startup cost ($) | Initial state
Alpha | 10 | 20 | 10 | 100 | ON
Beta | 5 | 30 | 12 | 100 | ON
Gamma | 5 | 50 | 13 | 100 | OFF
Delta | 10 | 20 | 20 | 0 | OFF
Unit Name |  |  | Marginal cost ($/MWh) | Startup cost ($) | Initial state
Alpha | 10 | 20 | 10 | 100 | ON
Beta | 5 | 30 | 12 | 100 | ON
Gamma | 5 | 50 | 13 | 100 | OFF
Delta | 10 | 20 | 20 | 0 | OFF
Hour | 1 | 2 | 3 | 4
Load (MW) | 30 | 40 | 60 | 50

## Slide 123
Example 6.14: Unit commitment with reserve
Hour | 1 | 2 | 3 | 4
 | 20 | 20 | 20 | 20
 | 10 | 20 | 30 | 30
 | 0 | 0 | 0 | 0
 | 0 | 0 | 10 | 0
Hour | 1 | 2 | 3 | 4
 | 20 | 20 | 20 | 20
 | 10 | 20 | 30 | 30
 | 0 | 0 | 0 | 0
 | 0 | 0 | 10 | 0
UC solution without reserve constraint:
Hour | 1 | 2 | 3 | 4
Headroom | 20 | 10 | 10 | 0
Total headroom:
Not enough headroom to meet a reserve requirement of 20 MW at hours 2, 3, and 4

## Slide 124
Hour | 1 | 2 | 3 | 4
 | 20 | 20 | 20 | 20
 | 10 | 10 | 30 | 25
 | 0 | 10 | 10 | 5
 | 0 | 0 | 0 | 0
Hour | 1 | 2 | 3 | 4
 | 20 | 20 | 20 | 20
 | 10 | 10 | 30 | 25
 | 0 | 10 | 10 | 5
 | 0 | 0 | 0 | 0
Example 6.14: Unit commitment with reserve
UC solution without 20 MW reserve constraint:
Bring Gamma online to meet the reserve requirement. No longer need Delta.

## Slide 125
Hour | 1 | 2 | 3 | 4
 | 15 | 20 | 20 | 20
 | 10 | 10 | 15 | 25
 | 5 | 10 | 15 | 5
 | 0 | 0 | 10 | 0
Hour | 1 | 2 | 3 | 4
 | 15 | 20 | 20 | 20
 | 10 | 10 | 15 | 25
 | 5 | 10 | 15 | 5
 | 0 | 0 | 10 | 0
Example 6.14: Unit commitment with reserve
Enforce a maximum ramp up rate of 20 MW/h on Alpha, Beta, and Delta, and of 5 MW/h on Gamma:
Adding constraints increases the cost of the schedule:
 | Cost ($)
Base Case | 2080
Add reserve constraint | 2125
Add max ramp rate constraint | 2225