## Slide 1: Chapter 3: Primary Energy Conversion

## Slide 2: Primary energy sources
Renewable sources
  Wind
  Solar
  Geothermal
  Wave
  Tidal
Fossil fuels
  Nuclear
  Coal
  Gas
  Oil

## Slide 3: Wind generation

## Slide 4: How much energy is there in the wind?
Area swept by the blades:
Mass of air passing through this area in time :
: specific mass of air
: wind speed
Kinetic energy in this mass:

## Slide 5: How much power is there in the wind?
Power in this wind:
Increases rapidly with:
  The wind speed
  The length of the blades

## Slide 6: How much power can be captured?
Capturing all of is impossible
: coefficient of performance
= Betz limit

## Slide 7: Flow of air around an airfoil
Airflow deflected down
Airfoil pushed up

## Slide 8: Lift force
Airfoil deflects the airflow down
Airfoil exerts a downward force on the air
Newton’s third law: action – reaction
Air exerts an upward force on the airfoil
This lift force makes it possible for airplanes to fly

## Slide 9: Torque
Lift force on each turbine blade
Creates a torque on the shaft of the turbine:
: wind power captured by the blades
: Rotational speed of the turbine shaft

## Slide 10: Angle of attack
Wind direction
Chord of the airfoil

## Slide 11: Lift force vs. angle of attack a
Lift force
Angle at zero lift
a

## Slide 12: Pitch angle
Angle of attack depends on the wind direction
is thus hard to measure
Pitch angle is the angle between the vertical and the chord
We can control by adjusting

## Slide 13: Controlling the pitch angle
Pitch angle can be adjusted by rotating the blade where it connects to the shaft

## Slide 14: Tip speed ratio
  : speed of the tip of the blade
  : wind speed
  : rotational speed
  : length of the blades

## Slide 15: Optimal tip speed ratio
too small:
   Too much wind passes through the turbine without being affected by the blades
too large:
  Because blades follow each other too closely, turbulence does not have time to dissipate
  Lowers the coefficient of performance

## Slide 16: Controlling a wind turbine
Adjust pitch angle and tip speed ratio
Maximize extraction of wind power
Avoid mechanical damage

## Slide 17: Power vs. wind speed characteristic
Ramp down
Cut-out speed
Wind power
Turbine Power
Rated
Power
Cut-in speed
Ramp up
Wind speed
Power

## Slide 18: Wind resource of the United States.
Source: C. Draxl, B.M. Hodge, A. Clifton, and J. McCaa. 2015. Overview and Meteorological Validation of the Wind Integration National Dataset Toolkit,
Technical Report, NREL/TP-5000-61740. Golden, CO: National Renewable Energy Laboratory.

## Slide 19: Variability of wind generation
Percentage of the aggregated load in the ERCOT system supplied by wind generation on November 16, 2018
Rather extreme day
Variability must be compensated by other sources
Chart: Time of Day
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
 | 30.143 | 28.5363 | 27.4435 | 25.1923 | 22.1254 | 18.5227 | 13.8013 | 10.4559 | 8.4748 | 5.3592 | 3.4692 | 3.486 | 4.6904 | 8.1409 | 12.4652 | 15.4287 | 17.3316 | 15.2039 | 20.2785 | 30.3892 | 36.5542 | 41.7322 | 43.8484 | 43.8133
Source: http://www.ercot.com

## Slide 20: Histogram of wind generation output
Histogram of the wind generation output in the ERCOT system in 2018
Overall wind generation capacity factor for 2018: 36.6%
Chart: 
| 0-20% | 20-40% | 40-60% | 60-80% | 80-100%
 | 0.24966 | 0.32158 | 0.26941 | 0.15662 | 0.0027397
Percentage of wind generation capacity
Frequency
Source: http://www.ercot.com

## Slide 21: Offshore wind

## Slide 22: Offshore wind

## Slide 23: Offshore wind
Beiter et al., “Expert perspectives on the wind plant of the future”, Wind Energy. 2022;1-16

## Slide 24: Thermal generation

## Slide 25: Heat engine
: Thermal energy to the prime mover
: Thermal energy wasted
: Energy converted to mechanical form
: Absolute temperature of the heat source
: Absolute temperature of the heat sink
Waste heat
Prime
Mover
Heat Source
Heat
Sink
Mechanical Energy

## Slide 26: Carnot Efficiency
Maximum theoretical efficiency
Practical efficiency much lower
To increase efficiency:
  Raise
  Lower
: Thermal energy to the prime mover
: Thermal energy wasted
: Energy converted to mechanical form
: Absolute temperature of the heat source
: Absolute temperature of the heat sink

## Slide 27: Fossil-fueled steam plants
Electrical energy
Boiler
Steam
turbine
Generator
Fuel
(e.g., coal)
Condenser
Steam
Generator
Pump
Low pressure
water
Heat
sink
Boiler
Heat
source
Low pressure
steam
High pressure
water
High pressure
steam
Condenser is required because pressuring
steam requires much more energy
than pressuring water

## Slide 28: Example 3.1: Efficiency of a coal plant
In a sub-critical coal generating plant, the temperature of the steam as it leaves the boiler and enters the turbine is 565°C. The temperature of the water as it exits the condenser is 20°C.
The Carnot efficiency of this plant is:
Practical efficiency of such a plant is typically around 39%.

## Slide 29: Coal power plant

## Slide 30: Steam turbine

## Slide 31: Input/output curve of a thermal power plant

## Slide 32: Example 3.2: Heat rate and CO2 emissions
According to the United States Environmental Protection Agency, the average, annual operating heat rate of U.S. coal-fired power plants is approximately 10,400 BTU/kWh.
To generate a constant 500 MW, a power plant would therefore have to produce 5.2 109 BTU of heat every hour, which would require burning about 168,477 kg (371,429 pounds) of coal.
This plant would release 481,845 kg (1,062,360 pounds) of CO2 each hour.

## Slide 33: Nuclear power plants
Generator
Turbine
Condenser
Pump
Boiler
Steam
Generator
Heat
Exchanger

## Slide 34: Nuclear power plant

## Slide 35: Concentrated solar plant
Electrical energy
Steam
turbine
Generator
Condenser
Pump
Heliostats
Receiver
Working fluid
Water
Heat Exchanger
Hot Tank
Cold Tank

## Slide 36: Combined heat and power plants - cogeneration
Boiler
Steam
turbine
Generator
Fuel
Condenser
Steam
Generator
Pump
Boiler
Heat
Recovery
Electrical energy
District heating or
Industrial processes

## Slide 37: Open cycle gas turbine (OCGT)
Cheap to build
Expensive to operate because inefficient
Highly flexible (fast start, quick ramp up and down)
Electrical energy
Generator
Compressor
Gas turbine
Gas
Exhaust gas at atmospheric pressure (still quite hot)
Cold air at high
pressure
Hot air at high
pressure
Combustion
chamber
Heat
sink
Heat
source
Cold air at
atmospheric
pressure

## Slide 38: Gas turbine
Picture: General Electric

## Slide 39: Combined cycle gas turbine (CCGT)
Electrical energy
Generator 1
Compressor
Gas
Combustion
chamber
Pump
Electrical energy
Generator 2
Condenser
Steam
Generator
Steam
Turbine
Exhaust - Heat source for steam cycle
Gas turbine
High overall efficiency: 63%

## Slide 40: Hydroelectric generation
Grand Coulee Dam Washington State, USA

## Slide 41: Impoundment hydro plants
Generator
Reservoir
Penstock
Discharge
Turbine
Gate
Head
Dam
Tailrace

## Slide 42: Grand Coulee Dam

## Slide 43: Tailrace of Grand Coulee Dam

## Slide 44: Turbine hall of Grand Coulee Dam

## Slide 45: Francis turbine

## Slide 46: Kaplan turbine

## Slide 47: Pelton turbine

## Slide 48: Three Gorges Dam on the Yangtze River

## Slide 49: Itaipu Dam (Brazil & Paraguay)

## Slide 50: Energy in an impoundment reservoir
Potential energy per unit of volume of water:
: specific mass of water (kg/m3)
: acceleration of gravity (m/s2)
: head (m)
Total potential energy:
: volume of the reservoir (m3)
Generator
Reservoir
Penstock
Discharge
Turbine
Gate
Head
Dam
Tailrace

## Slide 51: Example 3.3: Energy in a hydro reservoir
The reservoir behind the Grand Coulee dam in Washington State has a volume of 9,562,000 acre-ft (12 km3). However, only 5,185,400 acre-ft (6 km3) are considered “active” i.e., can be used for power generation. The hydraulic head is 116 m.
The useable potential energy in this reservoir is thus approximately:
Approximately the amount of energy that the consumers of the city of Seattle use in 10 weeks.

## Slide 52: Power from a hydro plant
Power in the water:
: Water flow rate (m3/s)
Power produced by the turbine:
: turbine efficiency (~90%)

## Slide 53: Controlling hydro power
Hydro is highly flexible
  Quick start
  Fast ramp up and ramp down
Turbine efficiency drops quickly when flow is off nominal
  Install multiple small turbines
  Operate each turbine at nominal flow or turn it off

## Slide 54: Columbia river system
Operation of upstream dams affects the downstream dams
Environmental constraints
  Effect on fish population
Interactions with other uses of water
  Flood control
  Irrigation
  Transportation
  Recreation
Scheduling hydro production is a very complex problem

## Slide 55: Diversion hydro plants
“Run-of-the-river” hydro
Power production depends on water flow in the river
Much smaller environmental impact that impoundment hydro

## Slide 56: Photovoltaic generation

## Slide 57: Solar resources in the United States
Global horizontal
solar irradiance (W/m2)
Source: Sengupta, M., Y. Xie, A. Lopez, A. Habte,
G. Maclaurin, and J. Shelby. 2018. "The National Solar Radiation Data Base (NSRDB)."
Renewable and Sustainable Energy Reviews 89 (June): 51-60.

## Slide 58: Solar cell
P-Type
Base
N-Type
Load
Sun
-
-

## Slide 59: and characteristics of a solar cell
Maximum power point

## Slide 60: Effect of irradiance on the characteristic
0.1
0.2
0.3
0.4
0.5
0.6
0
0
0.3
0.6
0.9
1.2
1.5
1.8
2.1
2.4
Voltage (V)
Power (W)
1000 W/m2
800 W/m2
600 W/m2
400 W/m2
200 W/m2

## Slide 61: Effect of temperature on the characteristic
Source: https://www.pvresources.com/en/solarcells/solarcells.php

## Slide 62: Maximizing solar generation
Maximum power point depends on:
  Irradiance
  Temperature
Operating at fixed voltage, fixed current or fixed resistance therefore does not maximize the efficiency of the cell.
Must adjust the voltage to track the maximum power point
  See chapter on power electronics energy conversion
Each solar cell produces at best a small voltage and current
  Connect cells in series to increase the voltage
  Connect cells in parallel to increase the current

## Slide 63: Example 3.4: PV array
A small PV array consists of two parallel columns of four panels connected in series. Each of these panels comprises 4 rows of 9 cells connected in series. Each cell produces a maximum of 2.5W at 0.5V. Calculate the voltage, current and power rating of this array.
The voltage in each row of a panel is .
The maximum power produced by each panel is .
The current produced by each panel is then: .
Since each column of the array consists of four panels in series, the voltage rating of the array is:
.
Since there are two columns in parallel, the current rating of the array is:
Finally, the power rating is given by:

## Slide 64: Solar tracking
Concept: rotate the solar panel to maximize irradiance
Horizontal axis rotation to track solar elevation
Vertical axis rotation to track solar azimuth
~50% of utility-scale solar installations use single-axis tracking
A few utility-scale solar installations use two-axis tracking
Remainder and most residential solar installations do not use tracking
Efficiency gain must be weighed against higher cost

## Slide 65: Vertical axis tracking
Source: Vinaykumar8687 through Wikimedia

## Slide 66: Horizontal axis tracking
Source: Vinaykumar8687 through Wikimedia

## Slide 67: Energy storage

## Slide 68: Pumped hydro plant
Generator/Motor
Upper Reservoir
Turbine/Pump
Lower Reservoir
Power House
Pumping mode
Generating mode

## Slide 69: Pumped hydro plant
Large power ratings: 100’s to 1000’s of MW
Typically stores enough water to discharge at full MW capacity for 6-8 hours
Typical roundtrip efficiency 70-80%
Construction cost is large

## Slide 70: Rocky Mountain Hydroelectric Plant (Georgia)

## Slide 71: Hohenwarte II in Thuringia, Germany

## Slide 72: Battery energy storage systems (BESS)
Power Conversion
System
BMS
Controller
Battery Cells
dc
ac
External
Commands

## Slide 73: Battery energy storage systems
Battery cells arranged in series and parallel
  Achieve suitable current and voltage ratings
Bidirectional power electronics converter
Battery management system (BMS)
  Monitors currents, voltages, temperatures of the battery cells
  Balance loading during charging and discharging
  Maintain safe operating condition

## Slide 74: BESS characteristics
Energy rating (MWh)
Power rating (MW)
Roundtrip efficiency (~80% typically)
State of Charge (SoC): percentage of energy rating available
Battery degradation
  Typically, 75% of energy capacity remains after 10 years
C-rate
  C = 1 means that a fully charged battery is discharged in one hour
  Faster charge/discharge rates reduce the battery life

## Slide 75: Example 3.5: Battery energy storage system
The BESS of Snohomish PUD’s Arlington microgrid is rated at 1MW, 1.38 MWh.
The cells are arranged in 11 parallel racks of 9 modules in series.
The voltage on the dc side varies between 1,126 V and 1,461 V depending on whether the battery is charging or discharging.
The voltage on the ac side is 630 V.
It is housed in a container that weighs 55,000 pounds.

## Slide 76: Other energy storage technologies
Flywheels rotating at up to 100,000 rpm
Compressed air combined with gas turbines
Use surplus renewable energy to electrolyze water and produce “green hydrogen”.
  Burning this hydrogen to generate electricity is not economically viable due to low thermodynamic efficiency.

## Slide 77: Applications of energy storage
Arbitrage – “Buy low – Sell high”
  Charge when renewable energy is abundant, and demand is low
  Discharge when demand is high and renewable energy is scarce
  Requires a large price difference to compensate for losses
Frequency regulation
  Compensate for small fluctuations in load and generation
Reserve services
  Compensate for a sudden loss of generation
Peaking generation
  Provide power during periods of high demand

## Slide 78: Choosing a generation technology

## Slide 79: Factors affecting the choice of technology
Local availability of primary energy
  Hydro, fossil fuel, nuclear, wind, solar
Self-reliance vs. imports
Mandates for use of renewable sources
Economic considerations
  Profitability

## Slide 80: A simple profitability calculation model
Simplifying assumptions:
  Consider a single year
  Ignore uncertainties
Profit :
  : sale price of electrical energy
  : amount of energy produced by the plant in one year
  : Cost of ownership of the plant
    Annuitized investment cost + operating cost

## Slide 81: Cost of ownership
capacity of the plant (MW)
in $/MW
in $/MWh
: Expected capacity factor of the plant
Annuitized
investment
cost
Operating
cost

## Slide 82: Breakeven price
Profit per MW of installed capacity (ignoring economies of scale):
Energy price at which the plant breaks even:

## Slide 83: Competitiveness
To be competitive, a technology with a high investment cost must have:
A low operating cost
A large capacity factor

## Slide 84: Example 3.6: Breakeven energy prices
 | ($/MWh) | ($/MW) |  | (h) | ($/MWh)
Wind farm | 0 | 140000 | 40% | 3504.0 | 39.95
CCGT | 26.5 | 88200 | 87% | 7621.2 | 38.07
Wind farm | 0 | 140000 | 40% | 3504.0 | 39.95
CCGT | 26.5 | 88200 | 87% | 7621.2 | 38.07

## Slide 85: Levelized cost of energy (LCOE)
Combines more rigorously operating and investment costs
($/MWh)
: expected life of the plant (years)
: expected investment cost in year ($)
: expected maintenance cost in year ($)
: expected fuel cost in year ($)
: expected energy production in year (MWh)
: discount factor to reflect the time value of money

## Slide 86: LCOE estimates
Plant type | Capacity factor (%) | LCOE ($/MWh)
Ultra-supercritical coal | 85 | 76.44
CCGT | 87 | 38.07
OCGT | 30 | 66.62
Advanced nuclear | 90 | 74.88
Geothermal | 90 | 35.43
Biomass | 83 | 94.83
Wind, onshore | 40 | 39.95
Wind, offshore | 44 | 122.25
Solar photovoltaic | 29 | 33.12
Hydroelectric | 59 | 52.79
US EIA estimates of the unweighted LCOE for new generation resources entering service in 2025 (2019 dollars)
(Source: www.eia.gov/aeo/pdf/electricity_generation.pdf)