## Slide 1: Chapter 8: Power Flow

## Slide 2: What is power flow analysis?
Generators inject power at various nodes of the network
Loads extract power from various nodes of the network
There are multiple paths between generation and loads
We don’t control directly how much power flows in each line
For given power injections and extractions, we must be able to check that the flows and voltages will be acceptable
B
C
D
E
A

## Slide 3: What is special about power flow analysis?
Variables in conventional DC circuit analysis:
  Voltages
  Currents
Variables in conventional AC circuit analysis:
  Magnitude and phase of voltages
  Magnitude and phase of currents
Variables in power flow analysis:
  Magnitude and phase of voltages
  Active and reactive powers

## Slide 4: Why use powers as variables?
Generators
  Convert mechanical power into electrical power
  Paid to supply power rather than current
Loads
  Power is what consumers are buying
  Easier to add powers than combine loads modeled as parallel impedances
Consequence:
  Product of variables  non-linear equations

## Slide 5: Overview
Develop an intuitive understanding of the relation between active and reactive power flows and voltages
Develop the mathematical formulation of the power flow problem
Develop a solution technique for the non-linear power flow equations
Discuss techniques for controlling flows and voltages
Discuss applications of power flow computations

## Slide 6: Develop an intuitive understanding of flows and voltages

## Slide 7: Intuitive understanding of flows and voltages
Consider one line somewhere in the system
: Sending end voltage
: Receiving end voltage
: Active and reactive power in the line at the sending end
Rest of the system

## Slide 8: Powers and voltage drops

## Slide 9: Powers and voltage drops

## Slide 10: Powers and voltage drops
causes most of the voltage difference in angle between and
causes most of the voltage difference in magnitude between and

## Slide 11: Powers and voltage drops
For typical transmission lines:
For typical distribution lines: to
  is reasonable for transmission but not for distribution

## Slide 12: Powers and voltage drops
The flow of reactive power causes most of the drop in voltage magnitude
The flow of active power causes most of the phase angle difference

## Slide 13: Active power flow and voltage angle
Large active power flows cause large phase angle differences
This can cause stability problems

## Slide 14: Reactive power flow and voltage magnitude
Large reactive power flows create large voltage drops
This can also create stability problems

## Slide 15: Active and reactive powers can flow in opposite directions
lags
with

## Slide 16: Reactive compensation
Large  large 
Inductive load:
Reactive compensation:
small 
capacitor bank, generator or SVC

## Slide 17: Reactive power “losses” in lines and transformers
Active power losses in the line:
Reactive power “losses” in the line:
These reactive power “losses” do not represent a loss of energy!
However, this reactive power losses must be supplied by a generator or through reactive power compensation

## Slide 18: Reactive power production in lines
For long Extra High Voltage (EHV) lines, the shunt capacitive reactances of the line model are significant
They produce reactive power:

## Slide 19: Reactive power in lines
Normally  is roughly constant
Lightly loaded line  is small  line produces reactive power
Heavily loaded line  is large  line absorbs reactive power

## Slide 20: Nodal Analysis

## Slide 21: Solving large networks
Power networks usually involve thousands of nodes and branches
We need to develop:
  A systematic method for building the equations
  An efficient method for solving these equations
 Nodal analysis

## Slide 22: Nodal analysis using an example
+
-
+
-
Network of lines
and transformers
Load
Generator
Generator
Ground

## Slide 23
First solve this example the long way using KCL and Ohm’s law
Generalize the results to derive a much simpler technique

## Slide 24: Step 1: Convert voltage sources to current sources
Thevenin model
Norton model

## Slide 25: Step 1: Convert voltage sources to current sources
+
-
+
-

## Slide 26: Step 1: Convert voltage sources to current sources

## Slide 27: Step 2: Convert all impedances to admittances

## Slide 28: Step 3: Number the nodes
0
3
2
1
4

## Slide 29: Step 4: Write KCL at each node
0
3
2
1
4

## Slide 30: Step 4: Write KCL at each node
0
3
2
1
4

## Slide 31: Step 5: Express branch currents in terms of node voltages
0

## Slide 32: Step 5: Express KCL in terms of the node voltages

## Slide 33: Step 5: Express KCL in terms of the node voltages
Group the terms according to the voltages

## Slide 34: Step 6: Put these equations in matrix form
=

## Slide 35: Final form of the nodal voltage equations
=
Admittance matrix
Unknown
nodal
voltages
Source currents

## Slide 36: Solving these equations
System with N busses
N equations
  KCL at each bus
N unknowns
  Nodal voltages
If exists:
0

## Slide 37
What is the structure of
the admittance matrix?
0

## Slide 38
Rows and columns of correspond to nodes of the network
Diagonal element :
  Sum of the admittances connected to node
Off-diagonal element :
  Minus admittance between nodes and
Given the network data, we can build the admittance matrix directly
0

## Slide 39
The diagonal elements are never zero
  There is always at least one branch connected to each node
The admittances to ground only appear in the diagonal elements
A linear combination of rows and columns will never add to zero
The admittance matrix is never singular
always exists
0

## Slide 40: Admittances between nodes and ground
Parallel admittances of sources
Loads
Shunt admittances of lines
B
B
R
X

## Slide 41: Terms of the admittance matrix
DC networks
  Branches have a real-valued resistance
   Branches have real-valued admittances
   All the terms of the admittance matrix are real
AC networks
  Branches have complex-valued impedances
   Branches have complex-valued admittances
   All the terms of Y are complex
Inverting a complex matrix is just as feasible as inverting a real matrix
  Particularly with a computer!

## Slide 42: Example 8.1
Build the nodal equations of the DC network shown below.
+
-
1
2

## Slide 43: Example 8.1
Convert voltage sources to current sources and impedances to admittances
+
-
1
2
1
2

## Slide 44: Example 8.1
Nodal equations
1
2

## Slide 45: Example 8.2
Build the nodal equations of the DC network shown below.
+
-
-
+

## Slide 46: Example 8.2
1
2
3

## Slide 47: Example 8.3
Build the nodal equations of the AC network shown below.
1
2

## Slide 48: Example 8.3
Convert voltage source to current source and impedances to admittances
1
2


## Slide 49: Example 8.4
Build the nodal equations of the AC network shown below.
line model
1
2

## Slide 50: Example 8.4
Convert voltage source to current source and impedances to admittances
1
1

## Slide 51: Example 8.4
1
2

## Slide 52: Admittance matrix of a modified network
Opening and closing switches changes the topology of the network
How do the equations change when:
  A line is connected between nodes i and j ?
  A line is disconnected between nodes i and j ?
  A source is connected at node k ?
Network
i
j
k

## Slide 53: Adding a line between nodes i and j
is the series impedance of the line
Network
R
X
is the series admittance of the line
is the shunt admittance at each end of the line

## Slide 54: Removing a line between nodes i and j
is the series impedance of the line
Network
R
X
is the series admittance of the line
is the shunt admittance at each end of the line

## Slide 55: Adding a source at node k
Network
i
j
k

## Slide 56: Example 8.5
1
2
3
Modify the admittance matrix built in Example 8.2 to reflect the removal of the
admittance between nodes 1 and 3

## Slide 57: Example 8.5
1
2
3
1
2
3

## Slide 58: Example 8.6
Modify the admittance matrix built in Example 8.2 to reflect the addition of a 2S
admittance between nodes 1 and 2
1
2
3

## Slide 59: Example 8.6
1
2
3
1
2
3

## Slide 60: Solving the nodal equations
We have a systematic method for forming the nodal equations
Systematic = something that a computer can handle
Need a systematic method for solving these equations
Three steps:
  LU factorization
  Forward solution
  Backward solution

## Slide 61: LU Factorization
Any non-singular matrix can be decomposed into the product of a lower triangular matrix and an upper triangular matrix

## Slide 62: How do we decompose A into A= LU?
Proceed by row
Processing each element determines the unknown shown in red

## Slide 63: Forward and Backward Solutions

## Slide 64: Example (1)
Assume that we have factorized the matrix
Hence, we must solve:

## Slide 65: Example (2)
Replacing in the complete equations, we get:
This is a set of equations in
It is easy to solve because it
is triangular
The are new unknowns
They are related to the original
unknowns through these
equations

## Slide 66: Example (3)
The forward solution of has given us the values of .
We can now solve the following system of equations for :
The solution proceeds from the bottom (backwards) because the matrix is upper triangular.
Done!

## Slide 67: Advantage of LU factorization
If needs to be solved for multiple right hand side vectors , the factorization does not need to be repeated
Since the factorization is the most time-consuming part of the process, this makes repeat solutions very efficient

## Slide 68: Sparsity of the admittance matrix
Consider a network with 1500 buses
Size of : 1,500 x 1,500
Number of elements: 2,250,000
Number of non-zero elements:
  On average each bus has three neighbors
  4 per row on average (diagonal + 3 neighbors) 4 x 1500 = 6,000 non-zeros
  Proportion of zero elements: 99.7%
is a sparse matrix
is still non-singular (invertible)
Solving is much faster if we take advantage of the fact that most of the terms are zero

## Slide 69: Sparsity Programming
Take advantage of the sparsity of the admittance matrix
  Store only the non-zero elements
  Carry out only the multiplications that involve non-zero elements
  Reduce the amount of memory needed
  Reduce the computing time required by not handling the zeros
All commercial power system analysis programs make use of sparsity programming
 They can solve networks with tens of thousands of nodes in seconds

## Slide 70: Mathematical formulation of the power flow problem

## Slide 71: Nodal power balance
Conventional nodal analysis:
Expresses Kirchhoff's Current Law or balance of current at each node
In power systems, we work with powers rather than currents
Formulate nodal analysis in terms of the balances of active and reactive powers at each node/bus

## Slide 72: Nodal power balance
Row of this matrix equation expresses KCL at node
Current injected at node
Sum of the currents flowing in the branches connected to node
Complex power injected
at node
: number of nodes in the network
Sum of the complex powers flowing in the branches connected to node

## Slide 73: A bit of complex algebra…
: element of the admittance matrix
: voltage at node
: voltage at node

## Slide 74: More complex algebra…
Let = difference in voltage phase angle between nodes and

## Slide 75: Finally…
: active and reactive powers injected at bus
Power flow equations

## Slide 76: Physical interpretation of the power flow equations
Bus
G
Generation at bus
Load at bus
Lines connecting bus to other buses
Active power injection at bus :
Reactive power injection at bus :

## Slide 77: The power flow equations
: Active power injection at bus
: Reactive power injection at bus
: Number of buses in the network
: Magnitude of the voltage at node
: Magnitude of the voltage at node
: Phase of the voltage at node
: Phase of the voltage at node
: Real part of term of matrix
: Imaginary part of term of matrix

## Slide 78: The power flow equations
N buses  2N equations
4N variables: at each node
Must have 2N unknown variables and 2N known variables
At each bus whether or is known or unknown depends on the type of bus
Three bus types:
  PQ bus
  PV bus
  Slack bus

## Slide 79: PQ bus
are given and thus known
are unknown
Buses with only a load are PQ buses

## Slide 80: Why model loads as constant P&Q?
132 kV
30 kV
Voltage regulator adjusts the taps to keep the voltage on the low voltage side constant as the transmission level voltage changes.
The consumers (and the loads) thus see a constant voltage. P&Q thus remain constant.
Note: more sophisticated load models are used in dynamic calculations

## Slide 81: PV bus
A generator typically:
  Produces a known amount of active power
  Maintains the voltage at its terminals constant
If there is a generator connected at bus :
  and are given and thus known
  and are unknown

## Slide 82: Slack bus – A bit of history
Under normal conditions, generation must be adjusted to match the load and keep the frequency constant at its nominal value
Secondary frequency control distributes these changes among all the generators
Before the invention of secondary frequency control, in each region all generators except one operated according to a fixed schedule
The remaining generator adjusted its output to keep the frequency constant using primary frequency control
In other words, this generator picked up the slack
The bus where it was located was the slack bus

## Slide 83: Why do we need a slack bus for the power flow?
Goal of the power flow:
  Given the powers injected by the generator and extracted by the loads, calculate the voltages and flows
Power flow models the steady state and thus assumes that the system is in balance and the frequency constant
Known
Known
Unknown because depends on the flows!
CONTRADICTION
Need to provide some slack generation

## Slide 84: Slack bus
Choose a generator bus as the slack bus
Leave unspecified
Since this is a generator bus, specify
Leave unspecified
Need one more specified variable
Need a reference for the angles
Set at the slack bus

## Slide 85: Numbers of equations and variables
N buses
2 N equations (2 at each bus)
4 N variables (at each bus)
2N known variables (2 at each bus):
  at PQ buses
  at PV buses
  at the slack bus
2N unknown variables (2 at each bus):
  at PQ buses
  at PV buses
  at the slack bus

## Slide 86: Example
Write the power flow equations for this system
j0.1
j0.2
j0.25
1
2
3
Figure shows the branch
impedances in per unit

## Slide 87: Y matrix
Figure shows branch admittances
-j10
-j5
-j4
1
2
3

## Slide 88: Power Flow Equations
Two equations for each bus
  First equation: balance of active power at that bus
  Second equation: balance of reactive power at that bus
Left hand side: power injected at the bus (> 0 for generation, < 0 for load)
Right hand side: power flowing in the branches
-j10
-j5
-j4
1
2
3

## Slide 89: Writing the equations for this system
(All the G terms are zero because we neglected the resistance of the lines)

## Slide 90: Simplifying the power flow equations

## Slide 91: Bus types
Bus 3:
P and V specified
Q and unknown
PV bus
Bus 1:
V and specified
P, Q unknown
Slack bus
Bus 2:
P and Q specified
V and unknown
PQ bus
1
2
3

## Slide 92: Two groups of equations
Equations where we know the injections: implicit equations
P equation of PQ bus
Q equation of PQ bus
P equation of PV bus
Equations where we don’t know the injections: explicit equations
P equation of slack bus
Q equation of slack bus
Q equation of PV bus

## Slide 93: Implicit Equations
Known variables:
Unknown variables:
P equation of bus 2
Q equation of bus 2
P equation of bus 3
Set of simultaneous non-linear equations
We need a technique to solve such equations

## Slide 94: Explicit Equations
Known variables:
Unknown variables:
P equation of bus 1
Q equation of bus 1
Q equation of bus 3
Solution of implicit equations:
Can calculate easily once we have solved the implicit equations to find

## Slide 95: Sparsity of the power flow equations
Equations for bus have a term involving only if or
Power flow equations have the same structure as the Y matrix
Very sparse set of equations

## Slide 96: Solving the power flow equations
The power flow equations are
  Implicit
  Non-linear
No direct, closed-form solution
Need to use an iterative solution technique
Newton-Raphson method
  Explain using single function of a single variable
  Generalize to system of N functions of N variables

## Slide 97: One-dimensional Newton-Raphson method
  Solve for where is a non-linear function of one variable
  Assume we know how to calculate:
    for any
    for any
x
f(x)

## Slide 98: Linear approximation
We can approximate a non-linear function by its tangent at point
The slope of this tangent is equal to the derivative of the function, at point :
x
f(x)
f ’()
x0

## Slide 99: Using the linear approximation
Assume that we can calculate and for any
x
f(x)
-

## Slide 100: Repeated linearization
x
f(x)
x1
x0
f ’()
f()
x2

## Slide 101: Formally: Taylor series expansion
Any continuous function can be expanded in a Taylor series:
Linear approximation of this function:
Replacing by its linear approximation:
Solving this linear approximation:
Solving by repeated linear approximation:

## Slide 102: Example
6
?
Find such that
Start with

## Slide 103: Example

## Slide 104: Example
?
=10
=7
-1.43

## Slide 105: Example

## Slide 106: Example
?
-0.49

## Slide 107: Example
0 | 6.000 | 10.00 | 7.000 | 1.429 | 4.571
1 | 4.571 | 2.039 | 4.142 | 0.492 | 4.079
2 | 4.079 | 0.242 | 3.157 | 0.077 | 4.002
3 | 4.002 | 0.06 | 3.004 | 0.002 | 4.000
0 | 6.000 | 10.00 | 7.000 | 1.429 | 4.571
1 | 4.571 | 2.039 | 4.142 | 0.492 | 4.079
2 | 4.079 | 0.242 | 3.157 | 0.077 | 4.002
3 | 4.002 | 0.06 | 3.004 | 0.002 | 4.000

## Slide 108
Notes: C:\Users_x\Miguel\Documents\UW_EE\Teaching\PSA\MAOV\Demos\Newton_Raphson\
s_fun_NR.m

## Slide 109
Notes: C:\Users_x\Miguel\Documents\UW_EE\Teaching\PSA\MAOV\Demos\Newton_Raphson\
s_fun_NR.m

## Slide 110
Notes: C:\Users_x\Miguel\Documents\UW_EE\Teaching\PSA\MAOV\Demos\Newton_Raphson\
s_fun_NR.m

## Slide 111: Example
6
4
Find such that
Starting from we get
1
What about the solution?

## Slide 112: x0 = 0
Notes: C:\Users_x\Miguel\Documents\UW_EE\Teaching\PSA\MAOV\Demos\Newton_Raphson\
s_fun_NR.m

## Slide 113: Convergence of iterative method
Convergence is not guaranteed!
Newton-Raphson method
  Can converge to the “wrong” solution
  Can diverge: iterative solution tends to infinity
  Can exhibit oscillatory behavior
An initial value close to the desired solution usually helps
When the function is well-behaved, the Newton-Raphson method usually converges quickly

## Slide 114: The power flow equations
N buses  2N equations
4N variables: at each node
Must have 2N unknown variables and 2N known variables
At each bus whether or is known or unknown depends on the type of bus
Three bus types:
  PQ bus
  PV bus
  Slack bus

## Slide 115: One-dimensional Newton-Raphson (NR) method
What about systems of N non-linear equations in N variables?

## Slide 116: Application of NR method to two functions of two variables
Taylor’s series expansion:
Let us neglect the higher order terms:

## Slide 117: Application of NR method to two functions of two variables
x
∆x
x0
Rewrite in matrix form:
Jacobian matrix

## Slide 118: Application of NR method to two functions of two variables
x
x1
x0
x2

## Slide 119: Example
Start from:
Iterative expression:

## Slide 120: Inverting a 2x2 matrix

## Slide 121: First iteration

## Slide 122: Second iteration

## Slide 123: Third iteration

## Slide 124: Fourth iteration
In general, we would not find an exact solution.
We would stop when the value of the functions is sufficiently small.
Stop because we have found a solution

## Slide 125: Newton Raphson method
Where the Jacobian matrix is:
3. Repeat until convergence
Given a set of non-linear equations:
2. Calculate correction
1. Linearize around

## Slide 126: Example: Two-bus power flow
Slack Bus
PQ Bus
Note: we can’t solve this problem directly because the powers are given at one end and the voltage magnitude at the other.
1
2

## Slide 127: Example: Two-bus power flow
1
2

## Slide 128: Example: Two-bus power flow
1
2

## Slide 129: Example: Two-bus power flow
1
2

## Slide 130: Example: Two-bus power flow
1
2

## Slide 131: Example: Two-bus power flow

## Slide 132: Example: Two-bus power flow

## Slide 133: Example: Two-bus power flow
We know and  Solve for and
(implicit equations)
Calculate and once we know and
1
2

## Slide 134: Solving the implicit equations
Rewrite these as follows:
and are called respectively the active and reactive mismatches because they represent the difference between the active and reactive power injected at a node and the active and reactive power flowing into this node through the branches.

## Slide 135: Jacobian of the power flow equations

## Slide 136: First Iteration
“Flat Start”
Non-zero mismatches
1
2

## Slide 137: First Iteration
“Flat Start”
Non-zero mismatches

## Slide 138: Second Iteration
Reduced mismatches
1
2

## Slide 139: Second Iteration

## Slide 140: Third Iteration
Mismatches almost small enough to stop
1
2

## Slide 141: Solution (after one more iteration)
1
2
Plug and in the explicit equations for the slack bus

## Slide 142: Example: Two-bus power flow
1
2

## Slide 143: Application of the NR method to the power flow
Powers flowing on the lines connected to node
Powers injected
at node
2N mismatch equations

## Slide 144: Generalization to N busses
System with buses  2N voltage magnitudes and angles:
Suppose bus is the slack bus
  =0
  is given and thus known
Assume that buses to are PV buses
  are given and thus known
There are then PQ buses
unknown voltage angles:
unknown voltage magnitudes:

## Slide 145: Newton-Raphson algorithm for power flow
Initialize
  Read input data
  Build the admittance matrix
  Choose starting point for voltages and angles
Until mismatches are sufficiently small, solve the implicit equations:
  Calculate the mismatches
  Build the Jacobian matrix
  Invert the Jacobian matrix
  Calculate the corrections
  Update the voltage magnitudes and angles
Using the explicit equations, calculate the active injection at the slack bus and the reactive injections at the PV buses
Calculate the line flows

## Slide 146: Implicit equations in mismatch form
…
…
equations
variables
Active power balance equations at the PQ and PV buses
Reactive power balance equations at the PQ buses

## Slide 147: Calculate the mismatches
…
…

## Slide 148: Build the Jacobian
…
…

## Slide 149: Invert the Jacobian and calculate corrections
…
…
…
…

## Slide 150: Update the voltage magnitudes and angles
…
…
…
…
…
…

## Slide 151: Terms of the Jacobian

## Slide 152: terms of the Jacobian matrix
For :

## Slide 153: terms of the Jacobian matrix
For :

## Slide 154: terms of the Jacobian matrix
For :

## Slide 155: terms of the Jacobian matrix
For :

## Slide 156: Calculating the lines flows

## Slide 157: Calculating the lines flows
because of the active and reactive losses

## Slide 158: Power Flow Applications

## Slide 159: Basic power flow functions
Calculate bus voltage magnitude and angle
Calculate line flows
Check voltages and flows against limits for all probable situations
Initialize other calculations (dynamics, faults)

## Slide 160: Applications in Planning
Look a few months to a few years ahead
Forecast the load at all busses
Forecast construction and retirement of generating plants
Calculate voltages and flows for various generation and load scenarios
  Peak load
  Light load
  Various lines and generating plants on outage
Are all voltages and flows OK under all these conditions?

## Slide 161: What if flows are too high?
Build more lines
Upgrade lines to higher nominal voltage
Build generating plants closer to the load center
Encourage energy efficiency to reduce load
Remote
Generation
Load
Center

## Slide 162: What if voltages are too low?
Build more lines
Upgrade lines to higher nominal voltage
Build plants closer to the load center
Encourage energy efficiency to reduce load
Add sources of reactive power closer to load
Remote
Generation
Load
Center

## Slide 163: What if voltages are too high?
Add sinks of reactive power close to the load center
Remote
Generation
Load
Center

## Slide 164: Applications in Operation
Look a few hours to a few months ahead
Adding new plants or lines is not an option
Must operate the existing system at minimum cost while maintaining system reliability
  Check normal conditions
    All equipment (except those on maintenance) are in service
  Contingency analysis

## Slide 165: Contingency analysis
Contingency: an event that might happen
  Sudden generator outage
  Sudden line or transformer outage
Credible contingency: an event that has a non-negligible probability of happening
  N-1 contingencies (loss of a single component) are much more likely than N-2 contingencies
Contingency analysis: perform a power flow for each credible contingency and check that the resulting state is still OK

## Slide 166: Active Power Flow Control
Used to correct excessive flow in lines
Generation re-dispatch
  Very effective but costly
Phase shifting transformers
  Introduce an artificial phase angle difference
  Act as “MW pumps”
Load shedding
  Used only as a last resort to avoid a system collapse

## Slide 167: Phase shifting transformer
Utility A
Utility B
Utility C
Suppose that utility A sells power to utility C.
Some of this power flows directly from A to C.
The rest flows from A to C through B.
This so-called “loop flow” may be undesirable

## Slide 168: Phase shifting transformer
Utility A
Utility B
Utility C
Phase shifter
By inserting a phase shifter on the tie-line between A and C, we can control the flow between these two utilities and ensure that the power flows directly between A and C and not through B.

## Slide 169: Reactive Power Flow Control
Used to correct voltage magnitude problems
Voltage set-point of generators
Tap-changing transformers
  Operate like “VAr pumps”
Reactive compensation
  Capacitors (mechanically or electronically controlled)
  Inductors (mechanically or electronically controlled)
  Synchronous condensers
Switch lines out of service to lower the voltages
  Remove shunt capacitance
Load shedding
  Used only as a last resort to avoid a system collapse

## Slide 170
Bus 1
Thermal
Solar
Solar
Wind
Thermal
Active flow or load (MW)
Reactive flow or load (MVAr)
-10.52
0.54
10
2
15
3.5
15
3.5
180
25
28.5
9.01
13.29
14.38
90.00
9.45
0.00
0.00
66.75
13.56
90.00
11.37
30.00
1.21
26.24
6.25
10.98
-4.73
-6.24
-7.05
-60.30
-3.82
-28.17
-8.99
Bus 2
Bus 3
Bus 4
Bus 5
0.00
-10.94
1.05
6.26
3.79
61.72
10.53
10.54
-3.09
-2.74
-0.96
-65.39
-5.32
-26.14
-6.87
2.74
-1.49
Example 8-11: Midday all lines in service
Slack bus
Load center
All voltages and flows are within limits
No need for reactive compensation

## Slide 171
Bus 1
Thermal
Solar
Solar
Wind
Thermal
Active flow or load (MW)
Reactive flow or load (MVAr)
-11.04
0.58
10
2.0
15
3.5
15
3.5
180
25
49.92
17.16
15.77
28.06
90.00
26.55
0
0
0
0
90.00
-5.27
30.00
11.74
38.58
15.31
42.39
-5.73
-18.58
-5.56
-92.75
-2.38
-48.90
-10.06
Bus 2
Bus 3
Bus 4
Bus 5
0
-41.79
7.02
18.68
3.30
96.29
22.85
11.06
-3.09
32.61
-3.04
0
0
-38.34
-12.56
Example 8-12: Midday, line 3-5 disconnected, overload on line 2-5
-32.35
3.29

## Slide 172
Bus 1
Thermal
Solar
Solar
Wind
Thermal
Active flow or load (MW)
Reactive flow or load (MVAr)
1.2
-0.25
55.56
17.40
45.33
25.54
60.00
27.33
41.93
15.20
33.97
-5.75
-21.93
-5.07
-83.92
-5.34
-54.42
-8.06
Bus 2
Bus 3
Bus 4
Bus 5
-33.59
5.14
22.06
3.26
86.81
21.65
-1.2
-2.72
41.03
-3.06
-41.66
-11.60
Example 8.13: Midday, line 3-5 disconnected,
decreased generation at 2,
and increased generation at 1 to remove overload on line 2-5
0
0
0
0
10
2.0
15
3.5
15
3.5
180
25
0
0
90.00
-5.31
30.00
12.13
0
-40.61
4.90

## Slide 173
Bus 5
Bus 1
Thermal
Solar
Solar
Wind
Thermal
Active flow or load (MW)
Reactive flow or load (MVAr)
53.37
23.92
10
2
15
3.5
15
3.5
250
40
80.85
36.92
208.14
90.99
0
0
0
0
48.57
12.46
0
0
90.0
35.86
40.92
86.04
-66.09
-14.29
-6.04
-7.07
-39.50
-7.68
-78.00
-10.76
Bus 2
Bus 3
Bus 4
0
67.86
26.36
6.06
3.80
40.24
10.42
-2.52
-0.40
2.52
-1.67
-47.69
-7.42
-84.81
-14.15
Example 8.14: Evening peak without corrective action
-52.72
-13.52

## Slide 174
Bus 5
Bus 1
Thermal
Solar
Solar
Wind
Thermal
Active flow or load (MW)
Reactive flow or load (MVAr)
40.58
0.91
10
2
15
3.5
15
3.5
250
40
72.11
18.18
171.30
30.80
0
0
35.00
33.58
52.78
18.69
0.00
0.00
90.00
14.34
81.30
19.83
-56.21
-1.67
-1.30
-7.49
-51.64
-13.70
-70.12
-1.09
Bus 2
Bus 3
Bus 4
20
57.31
7.59
1.31
4.12
48.66
9.22
-40.27
2.33
-7.45
-11.06
-47.89
-5.11
-80.35
-0.11
8.15: Evening peak with corrective actions
7.49
9.07

## Slide 175: Optimal Power Flow

## Slide 176: Power System Operation
Economic Dispatch
Load Forecast
System Load
Power Flow
Generation at each node
Load at each
node
Any flow over the limit?
Any voltage problem?
No
Yes
Need to fix the problems

## Slide 177: How do we fix problems?
How do we fix a problem at minimum cost?
How do we fix a problem without creating another problem?
  Example: Removing an overload on one line without overloading another
How do we fix all the problems at the same time at minimum cost?
Problem = violation of an inequality constraint
Formulation as an optimization problem
Optimal Power Flow (OPF)
  What values of the control variables minimizes the cost of operating the power system while satisfying the network constraints?

## Slide 178: Decision or control variables
Active power output of the generating units
Voltage at the generating units
Position of the transformer taps
Position of the phase shifter taps
Status of the switched capacitors and reactors
Set-point of power electronics (HVDC, SVC)
Topology of the network
Amount of load disconnected (as a last resort)
 Vector of control variables:

## Slide 179: State variables
Describe the response of the system to changes in the control variables
Magnitude of voltage at each bus
  Except generator busses, which are control variables
Angle of voltage at each bus
  Except slack bus
 Vector of state variables:

## Slide 180: Parameters
Known characteristics of the system
Network topology
Network parameters
  Flow and voltage limits
Load at each bus
Generator cost functions
Generator limits
Vector of parameters:

## Slide 181: Objective function
Examples:
  Minimize generation cost:
  Minimize change in control variables:

## Slide 182: Equality constraints
Power flow equations:
Compact notation:

## Slide 183: Inequality constraints
Limits on the control variables:
Operating limits on flows:
Operating limits on voltages:
Compact expression:

## Slide 184: Compact formulation of the OPF problem
Subject to:

## Slide 185: Solving the OPF problem
Very large optimization problem
  Many control variables
  Many inequality constraints
    Which ones are binding?
Non-linear objective function
Non-linear constraints
Requires powerful software optimization packages