## Slide 1: Chapter 4: Electromechanical Energy Conversion

## Slide 2: Example: steam plant
Electrical power
Boiler
Steam
turbine
Generator
Fuel
Condenser
Steam
Generator
Pump
Boiler
Mechanical power

## Slide 3: Structure of a generator
ROTOR
STATOR
a
a’
b
b’
c
c’
Axis of the a-a’ winding
Axis of the rotor
N
S
Airgap

## Slide 4: Magnetic fluxes linking the stator windings
Stator windings are 120° apart
: flux linkage
rotor flux
: effective number of turns
STATOR
ROTOR
a
a’
b
b’
c
c’
Axis of the a-a’ winding
Axis of the rotor
N
S

## Slide 5: Voltages induced in the stator windings
Rotor rotates at constant speed 
Stator flux linkages are time varying
Lenz’s law:
STATOR
ROTOR
a
a’
b
b’
c
c’
Axis of the a-a’ winding
Axis of the rotor
N
S

## Slide 6: Voltages induced in the stator windings

## Slide 7: Voltages induced in the stator windings
Have the same magnitude
  Proportional to the rotor flux
Have the same angular frequency
  Determined by the mechanical speed of rotation
Are exactly 120° out of phase in time
  Because the windings are shifted by 120° in space

## Slide 8: Number of magnetic poles
a
a’
b
b’
c
c’
N
S
Rotor with two magnetic poles
(or one pole pair)
a
a’
b
b’
c
c’
N
N
S
S
Rotor with four magnetic poles
(or two pole pairs)

## Slide 9: Frequency of induced voltages
a
a’
b
b’
c
c’
N
S
One mechanical rotation
induces one electrical period
a
a’
b
b’
c
c’
N
N
S
S
One mechanical rotation induces two electrical periods
because each stator winding ”sees” two North poles and two south poles

## Slide 10: Frequency of induced voltages
Generalization to rotor magnetic poles:
: electrical angular frequency
: mechanical angular frequency
: rotational speed in revolutions per minute (rpm)

## Slide 11: Typical rotational speed of generator
Steam and gas turbines are most efficient at high speed
  or
Hydro turbines are most efficient at low speed
Wind turbines rotate at speeds between 5 and 20 rpm
  Would require too many poles
  Use mechanical gearbox or power electronics

## Slide 12: Stator of a small generator

## Slide 13: Stator of a large hydro generator

## Slide 14: Installing the stator windings of a hydro generator

## Slide 15: Rotor of the generator for a thermal power plant
Picture: Ansaldo Energia

## Slide 16: Cutout of the generator for a thermal power plant
Picture: Ansaldo Energia

## Slide 17: Rotor of a large hydro generator

## Slide 18: Three-phase systems

## Slide 19: Why use three-phase systems?
Three-phase systems can produce a rotating magnetic field
  Three-phase motors start without the need for extra equipment
For the same physical size, a three-phase generator produces more power than a single-phase generator
Three-phase lines transmit more power
Power in a three-phase system does not pulsate at twice the frequency as it does in a single-phase system

## Slide 20: Three-phase sources
3 sets of windings  6 terminals
Connecting 6 wires over a long distance is expensive
We don’t need 6 wires to have a three- phase system
Y connection  use three or four wires
Delta connection  use three wires
a
a’
b
b’
c
c’
a
b
c
c’
b’
a’

## Slide 21: Y-connection
a
n
b
c
120°
120°
120°
a
a’
b
b’
c
c’
n
a
b
c
n

## Slide 22: Line-ot-neutral voltages
Balanced three-phase voltage phasors
  Equal magnitude
  Equal 120° phase differences
a
n
b
c
120°
120°
120°

## Slide 23: Line-to-neutral voltages
The sum of any set of balanced phasors is zero
a
n
b
c
120°
120°
120°

## Slide 24: Line-to-line voltages
n
c
b
30°
a

## Slide 25: Line-to-line voltages
n
c
b
30°
a

## Slide 26: Line-to-line voltages
Line-to-line voltages:
Balanced
times the magnitude of the line-to-neutral voltages
n
c
b
30°
a

## Slide 27: Line-to-line voltages
Because the neutral point n is not always accessible, three-phase voltages are usually specified in terms of their line-to-line magnitude
n
c
b
30°
a

## Slide 28: Delta connection
a
a’
b
b’
c
c’
a
b
c
a=c’
b=a’
c=b’
120°

## Slide 29: Delta connection
a=c’
b=a’
c=b’
120°

## Slide 30: Three-phase loads
N
A
C
B
Y-connected load
A
C
B
Delta-connected load
Balanced because same in each phase
Balanced because same in each phase

## Slide 31: Y-connected load connected to Y-connected source
a
b
c
n
N
A
C
B
KCL at node n or N:

## Slide 32: KVL around the a-A-N-n-a loop
a
b
c
n
N
A
C
B

## Slide 33: KVL around the b-B-N-n-b loop
a
b
c
n
N
A
C
B

## Slide 34: KVL around the c-C-N-n-c loop
a
b
c
n
N
A
C
B

## Slide 35: Y-connected three-phase system
because source is balanced

## Slide 36: Neutral current
a
b
c
n
N
A
C
B
KCL at node n or N: 
Neutral connection is not required if the system is balanced

## Slide 37: Unbalanced three-phase systems
Unbalanced source or unbalanced load
 if there is a connection between the neutrals
Actual systems are usually not perfectly balanced
  Single phase loads create unbalances
  Distribution networks are unbalanced because they serve single-phase loads
  Aggregating many unbalanced loads makes the system roughly balanced
Chapter 10 discusses techniques for analyzing unbalanced systems

## Slide 38: Unbalanced three-phase systems
Some neutral points are connected to ground (“grounded”)
However, never assume that or !
a
b
c
n
N
A
C
B

## Slide 39: Phase a of balanced system, ,
a
b
c
n
N
A
C
B

## Slide 40: Phase b of balanced system, ,
a
b
c
n
N
A
C
B

## Slide 41: Phase c of balanced system, ,
a
b
c
n
N
A
C
B

## Slide 42: Currents in a balanced system
a
b
c
n
N
A
C
B

## Slide 43: Currents in a balanced system
n
Reference
q
q
q
A balanced Y-connected load draws a balanced set of currents

## Slide 44: Example 4.1: Y-connected three-phase load
A balanced three-phase Y-connected load is supplied from a balanced three-phase voltage source with a line-to-line voltage of 480V. The impedance of each phase of the load is and the impedance of each line connecting the source to the load is .
a
b
c
n
N
A
C
B

## Slide 45: Example 4.1: Y-connected three-phase load
A balanced three-phase Y-connected load is supplied from a balanced three-phase voltage source with a line-to-line voltage of 480V. The impedance of each phase of the load is and the impedance of each line connecting the source to the load is .
V
V
A

## Slide 46: Example 4.1: Y-connected three-phase load
The complex power supplied by phase a of the source is:
VA
kW
kvar
kW
kvar
The complex consumed in phase A of the load is:
VA
kW
kvar
kW
kvar

## Slide 47: Delta-connected load
Apply KCL around the load:
A
C
B

## Slide 48: Delta-connected load
A
C
B

## Slide 49: Delta-connected load
KCL at nodes A, B, and C:
A
C
B
A balanced delta-connected load draws a balanced set of currents

## Slide 50: Example 4.2: Delta-connected three-phase load
A balanced three-phase Δ-connected load is supplied directly from a balanced three-phase voltage source with a line-to-line voltage of 480V. The impedance of each phase of the load is .
V
A
A
kVA
kW
kvar
kW
kvar

## Slide 51: -Y equivalence
A
C
B
A
C
B
Equivalent if = 

## Slide 52: Example 4.3: Parallel Y- and Δ-connected loads
A
C
B
A
C
B
, ,

## Slide 53: Example 4.3: Y-Δ equivalent
, ,
A
C
B
A
C
B

## Slide 54: Example 4.3: Per-phase analysis
Impedance in each phase:

## Slide 55: Powers in balanced three-phase systems
Power in each phase:
Power in balanced three-phase system
and depends on whether the load is Y- or Δ-connected
Need uniform way of calculating the powers
Express the powers in terms of line-to-line voltage and line current
Those quantities are easily accessible

## Slide 56: Powers in balanced three-phase systems
3-phase load
or
combination of
3-phase loads

## Slide 57: Powers in balanced three-phase systems
3-phase load
or
combination of
3-phase loads
Y-connected load  and
Δ-connected load  and

## Slide 58: Powers in balanced three-phase systems
3-phase load
or
combination of
3-phase loads

## Slide 59: Example 4.4: Power in a three-phase load
Calculate the line current drawn by a 10 kVA unity power factor three-phase load supplied from a 480V source

## Slide 60: Single-phase representation
Balanced system:
  Balanced source
  Balanced load
  Balanced connection between source and load
Symmetrical behavior in each phase
  “Three-phase” symmetry
Need to study only one phase

## Slide 61: One-line diagram
Graphical extension of single-phase representation
Every item represents a three-phase component
Balanced three-phase system  no need for a “return conductor”
Line
Transformer
Generator
Circuit breaker
Busbar
Load

## Slide 62: One-line diagram for a 39-bus system

## Slide 63: Per-unit system
Normalization of the various quantities
Simplifies the analysis
  Removes most factors
  No difference between single-phase and three-phase

## Slide 64: Example 4.5: Per-unit system
Voltage at a particular node is kV
Nominal or base value for voltages at that node is 132 kV
Per unit value of this voltage:
Per unit quantities are dimensionless
Normalization affects only magnitude of complex numbers

## Slide 65: Choosing the base quantities – Single-phase system
Choose a common base value for the powers
    Applies to the active, reactive, complex and apparent powers
    Applies to the entire system
    Arbitrary but typically a company standard applies e.g., 100 MVA
    Will be specified in homework assignments and exams
Choose the nominal or rated voltage for each area of the system as the base for all voltages in that area
    Different areas will have different base voltages
    If a voltage is close to its nominal value, its per unit voltage is close to 1.0 p.u.

## Slide 66: Example
Transformer
Generator
20kV/132kV
30kV/132kV
132kV/25kV

## Slide 67: Choosing the other base quantities – Single-phase system
Principle:
Relation between pu quantities = relation between SI quantities
Base current
    In SI quantities we have:
    In p.u. we want:
    Which can be written:
    Hence:

## Slide 68: Choosing the other base quantities – Single-phase system
Base impedance
    Ohm’s law in SI quantities:
    In pu we want:
    Which implies:
    =
  Base admittance:

## Slide 69: Summary of base quantities for single-phase systems
Quantity | Symbol | Rule
Apparent power |  | Arbitrary choice of one value for the entire system
Active power |  | 
Reactive power |  | 
Voltage |  | Nominal voltage at each location
Current |  | 
Impedance |  | 
Admittance |  | 
Quantity | Symbol | Rule
Apparent power |  | Arbitrary choice of one value for the entire system
Active power |  | 
Reactive power |  | 
Voltage |  | Nominal voltage at each location
Current |  | 
Impedance |  | 
Admittance |  | 

## Slide 70: Choosing the base quantities – three-phase system
Like single-phase but with a few twists
Choose a common base value for the powers
Choose the nominal or rated voltage for each area of the system as the base for all voltages in that area
    We also want:
    Which means:
    Since , we must have:

## Slide 71: Choosing the base quantities – three-phase system
Base current
    In pu we want:
    Which can be written:
    In SI quantities we have in a three-phase system:
    Which gives
    Hence:

## Slide 72: Choosing the base quantities – three-phase system
Base impedance
    Balanced Y-connected load:
    We would like to write:
    Which implies:
    Hence:

## Slide 73: Summary of base quantities – Three-phase systems
Quantity | Symbol | Rule
Apparent power |  | Arbitrary choice of one value for the entire system
Active power |  | 
Reactive power |  | 
Line-to-line voltage |  | Nominal line-to-line voltage at each location
Line-to-neutral voltage |  | 
Current |  | 
Impedance |  | 
Admittance |  | 
Quantity | Symbol | Rule
Apparent power |  | Arbitrary choice of one value for the entire system
Active power |  | 
Reactive power |  | 
Line-to-line voltage |  | Nominal line-to-line voltage at each location
Line-to-neutral voltage |  | 
Current |  | 
Impedance |  | 
Admittance |  | 

## Slide 74: Example 4.6: Base quantities
A small three-phase power system consists of two areas connected by a transformer. The nominal voltages is 132 kV in area Blue and 69 kV in area Red. Select base values for all quantities in both areas.
Let us choose . This choice applies to both areas.

## Slide 75: Example 4.7: Per unit currents
A load in area Blue of Example 4.6 draws 0.2 pu of apparent power at a voltage of 0.97 pu.
Calculate the line current drawn by this load in Amps.
Since , we have:

## Slide 76: Converting per unit impedances
Manufacturers give the values of the impedances in per unit calculated on the basis of the rating of the equipment
Must be converted to the per unit system used for system studies
Impedance values in Ohms don’t depend on the per unit basis:
Usually

## Slide 77: Example 4.8: Base impedance conversion
According to the data provided by its manufacturer, a device rated at 50 MVA has an impedance of 0.3 pu. This device must be studied as part of a system for which the base value for power is What value of impedance should be used for these system studies?

## Slide 78: Synchronous generator model
Rotor flux induces three-phase e.m.f. in the stator windings
is a function of
The stator windings have a resistance and an inductive reactance
The voltage at the terminal of the generator is:
STATOR
ROTOR
a
a’
b
b’
c
c’
N
S

## Slide 79: Single-phase model of a synchronous generator

## Slide 80: Single-phase model of a synchronous generator
Usually,

## Slide 81: Control of an isolated generator

## Slide 82: Control loops of an isolated generator
Load
Prime Mover
Shaft
Governor
Primary Energy
+
-
Exciter
+
-
Generator

## Slide 83: Operation of an isolated generator
The governor loop keeps the frequency constant
 mechanical power from prime mover follows the demand for active power

## Slide 84: Operation of an isolated generator
Generator supplies reactive power
Generator absorbs reactive power

## Slide 85: Operation of an isolated generator
: power factor angle
: power angle
Generator supplies active and
reactive power
Generator supplies active and
absorbs reactive power

## Slide 86: Synchronizing a generator to the grid
a’
b’
c’
a
b
c
Generator
Grid
Before closing the switch:
Same phase sequence
Same frequency
Same voltage magnitude
Minimal phase angle difference (small )

## Slide 87: Operating a small generator synchronized to the grid
Assume that the rating of the generator is small compared to the rest of the grid
The grid then sets
  The frequency (60 Hz)
  The voltage at the terminal of the generator ()
Model the grid as an ideal voltage source
We will consider more sophisticated grid models later
Generator
Grid

## Slide 88: Operating a small generator synchronized to the grid
Generator
Grid
=

## Slide 89: Power angle curve
Chart: 
Chart: 
(degrees)
Mechanical power supplied by the prime
mover

## Slide 90: Reactive power
is usually small  
The difference in magnitude between and determines the reactive power injection

## Slide 91: Reactive power
Larger
Injects a lagging current
Injects reactive power in the grid
“Overexcited”
Smaller
Injects a leading current
Absorbs reactive power from the grid
Same active power injection
“Underexcited”

## Slide 92: Example 4.9: Steady state generator operation
The prime mover of a generator provides 0.25 pu of power. Its synchronous reactance has a value of 0.8 pu and it operates at its nominal voltage. The value of the field current is such that the magnitude of the internal emf is 1.15 pu. Calculate the power angle, the reactive power produced by this generator and the power factor.

The current lags the voltage because this generator supplies reactive power.

## Slide 93: Example 4.10: Effect of the field current
Repeat the calculation of the previous example for the case where the value of the field current is such that the magnitude of the internal emf is 0.95 pu.

The current leads the voltage because the generator absorbs reactive power.

## Slide 94: Synchronous condenser
Synchronous generator not driven by a prime mover
Losses provided by the grid
Produces or absorbs only reactive power
Injects reactive power in the grid
Absorbs reactive power from the grid

## Slide 95: Generator limits
Maximum active power:
  Determined by prime mover
Minimum active power:
  Flame stability in the boiler
Stator current limit:
  Avoid damaging conductor insulation due to overheating
Field current limit: ≤
  Avoid damaging conductor insulation due to overheating
How to express as
a function of and ?

## Slide 96: as a function of and
 Circle in theplane

## Slide 97: ≤ as a function of and
≤


Circle or radius
centered at in the plane

## Slide 98: Loading capability diagram of a generator
Under-excitation
limit

## Slide 99: Simplified generator limits
Under-excitation
limit