## Slide 1
Chapter 5:
Electronic Power Conversion

## Slide 2
Why power electronics converters?
Thermal and hydro generation
  Mechanical power from prime mover is controllable
  Can control prime mover to rotate at constant speed
  Synchronous generator then produces constant frequency ac
Wind and photovoltaic power generation
  Primary power source is variable
  Wind: prime mover rotates at variable speed
  PV: no prime mover, produces dc instead of ac

## Slide 3
Why power electronics converters?
Convert dc into ac
Convert variable frequency ac into constant frequency ac
Control the amount of active power injected into the grid
Control the amount of reactive power injected into the grid
Extract power at one location in the grid and inject it at another via an HVDC link

## Slide 4
Ideal Switch
Switch closed: no voltage drop
Switch open: no current
Bidirectional:
  Power can flow in both directions
Can carry large currents when closed
Can block large voltages when open
Controllable
  Easy to turn on and off
  Fast switching for better power control
  Minimum amount of power to open or close the switch
Closed switch
Open switch
A switch that has all these characteristics has not yet been invented
No losses

## Slide 5
Reverse-conducting switching cell
Insulated-gate bipolar transistor (IGBT) antiparallel with a diode
Apply control signal to G:
  Current can flow from C to E
Apply control signal to G:
  Current from C to E is interrupted
Diode allows a current to flow from A to K
We will neglect voltage drops
Provides the functionality needed to build voltage source converters
G
C
E
A
K

## Slide 6
Single-phase H-Bridge converter
+
-
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
i
s4
s2
s3
Interface a dc subsystem with an ac subsystem

## Slide 7
Forbidden combinations of control signals
OR
These combinations of control signals create a short circuits the dc source
+
-
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
i
s4
s2
s3

## Slide 8
Current flows through Q1 and Q2
+
-
D1
Q1
s1
D2
Q2
dc subsystem
ac subsystem
i
s2
D4
Q4
s4
D3
Q3
s3

## Slide 9
Current flows through D1 and D2
+
-
D1
Q1
s1
D2
Q2
dc subsystem
ac subsystem
i
D4
Q4
s4
s2
D3
Q3
s3

## Slide 10
Current flows through D4 and D3
+
-
D1
Q1
s1
D4
Q4
D3
Q3
dc subsystem
ac subsystem
i
s4
D2
Q2
s2
s3

## Slide 11
Current flows through Q3 and Q4
+
-
D1
Q1
s1
D4
Q4
D3
Q3
dc subsystem
ac subsystem
i
s4
D2
Q2
s2
s3

## Slide 12
Operation of the single-phase H-Bridge converter
+
-
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
i
s4
s2
s3
The value of is thus independent of the direction of i
The polarity of is determined by the control signals

## Slide 13
as a function of the control signals
1
0
1
0
+
0
-

## Slide 14
Shaping
Equal duration for and
  Create a zero-average ac waveform
Duration of the control signals control the frequency of
Timing of the control signals controls the phase of
How do we control the magnitude of ?

## Slide 15
Pulse Width Modulation (PWM)
Chart: 
Triangular carrier
Sinusoidal modulator
Chart: 
Chart: 
1
Chart: 
Chart: 
1
0
0
Modulator < Carrier  = 1
Modulator > Carrier  = 1

## Slide 16
Pulse Width Modulation (PWM)
Chart: 
Chart: 
Chart: 
+
0
-
Triangular carrier
Sinusoidal modulator
PWM waveform
Fundamental of
PWM waveform

## Slide 17
Pulse Width Modulation (PWM)
Frequency of the carrier is constant
Frequency of the fundamental of the PWM waveform is determined by the frequency of the modulator
Chart: 
Chart: 
Chart: 
+
0
-

## Slide 18
Pulse Width Modulation (PWM)
Amplitude of carrier is constant
Amplitude of modulator determines amplitude of fundamental of PWM
Chart: 
Chart: 
Chart: 
+
0
-

## Slide 19
Pulse Width Modulation (PWM)
Amplitude of carrier is constant
Amplitude of modulator determines amplitude of fundamental of PWM

## Slide 20
Pulse Width Modulation (PWM)
We will consider only the fundamental of the PWM waveform
Filters are usually added to manage the harmonics
Chart: 
Chart: 
+
0
-

## Slide 21
Single-Phase H-Bridge converter
+
-
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
i
s4
s2
s3
fundamental component of PWM waveform
Phase-lock loop to synchronize and
adjustable phase difference between and

## Slide 22
Steady state converter model

## Slide 23
Active power control
Control the flow of active power by controlling the phase of the PWM waveform
 power flows from dc side to ac side
 power flows from ac side to dc side

## Slide 24
Reactive power control
Control the flow of reactive power by controlling the magnitude of the fundamental of the PWM waveform

## Slide 25
More realistic model of the dc subsystem
+
-
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
i
s4
s2
s3
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
s4
s2
s3
Power Source
Modeled as ideal dc voltage source
Constant voltage for any current
Can supply or absorb any amount of dc power
Power is variable
Example: PV panel
What happens if ?

## Slide 26
dc subsystem as a power source
D1
Q1
s1
D4
Q4
D3
Q3
D2
Q2
dc subsystem
ac subsystem
s4
s2
s3
Power Source
Energy stored in capacitor:
Capacitor serves as an energy buffer
is regulated to keep constant  follows

## Slide 27
Three-phase voltage source converter
D1
Q1
s1
D4
Q4
D5
Q5
D2
Q2
dc subsystem
ac subsystem
s4
s2
s5
Power Source
D3
Q3
D6
Q6
s6
s3

## Slide 28
Applications of Power electronics in Power Systems

## Slide 29
Battery energy storage
Converter
+
–
Grid
Battery

## Slide 30
Battery energy storage – active power
Battery between min and max state of charge  close to ideal voltage source
Charging battery  converter = rectifier
Discharging battery  converter = inverter
to avoid premature battery aging
Converter
+
–
Grid
Battery

## Slide 31
Battery energy storage – reactive power
Converter can supply or absorb reactive power
Limited by the converter current rating
Converter
+
–
Grid
Battery

## Slide 32
Photovoltaic (PV) generation
Converter
Grid
PV Array
is a complex function of the irradiance and the temperature of the cells
 The maximum value of changes constantly  need to adapt

## Slide 33
What value of gives ?
Two different values of solar irradiance

## Slide 34
Maximum Power Point Tracking
Converter
Grid
PV Array
MPPT

## Slide 35
Perturb and Observe technique
Maximum power point

## Slide 36
Perturb and Observe algorithm
Let be the measured value of at the current
Using the control of the converter, set
Let be the measured value of at this new
If set
Wait a short time
Go back to step 2

## Slide 37
Wind generation
Optimal turbine speed depends on the wind speed
Rotational speed of a synchronous generator is proportional to grid frequency
Connecting a wind turbine to the grid directly with a synchronous generator is not possible
Type 4 wind turbine
  Use the synchronous generator to produce variable frequency ac
  Rectify this ac into dc
  Convert dc into fixed frequency ac

## Slide 38
Type 4 wind turbine
Converter 1: Rectifier
+
-
Reg
Converter 2: Inverter
1:G
Gearbox
Reg
Wind Speed
Grid
Synchronous generator

## Slide 39
Type 4 wind turbine
Advantages
  Excellent controllability
  No slip rings if permanent magnet synchronous generator
  Direct drive turbines don’t use a gearbox
Disadvantage
  High cost because two converters rated at maximum power are needed
Technology of choice for largest wind turbines
  Offshore wind turbines in particular

## Slide 40
Type 3 wind turbine
Uses an induction generator rather than a synchronous generator
Induction generator
  Stator: three-phase windings like synchronous generator
  Rotor: three-phase winding
  Rotor speed is not fixed by the frequency of the voltage on the stator

## Slide 41
Induction generator
Synchronous speed is fixed by the grid frequency:
Mechanical speed of the rotor:
Slip : relative difference in speed between stator and rotor
determines the amount of power flowing out of the rotor windings
Angular frequency of the rotor currents:
stator
rotor
Grid

## Slide 42
Type 3 wind turbine
Mechanical power from wind turbine
Power through the stator
Induction Generator
Power through the rotor
Converter
Grid
Wind Turbine
Speed control

## Slide 43
Type 3 wind turbine
Rotor
1:G
Gearbox
Stator
Stator
Grid Side Converter
Transformer
Rotor Side Converter
Slip rings
Reg
Wind Speed
Grid

## Slide 44
Type 3 wind turbine
Advantages
  Since the rotor carries only a fraction of the rated power of the turbine, the ratings of the converters can be much smaller
Disadvantages
  Requires slip rings
  Requires a gearbox
Used for smaller wind turbines

## Slide 45
High Voltage dc links
Back-to-back link or dc line
Applications:
  Connection between two power systems operating at different frequencies
  Undersea power cables longer than 50 km
  Transmission of a lot of power over a long distance
Examples:
  dc intertie between the Pacific Northwest and Los Angeles
  dc links between US Eastern and Western interconnections
  Multiple cables under the North Sea and the Baltic Sea in Europe
  dc link between the 50Hz and 60HZ systems in Japan

## Slide 46
High Voltage dc Link
Converter 1
+
-
Reg
Converter 2
Grid 2
Grid 1
dc link